## Summary
Discipline | Checks | Document | Asset | Practice | Go and see | Reconcile | Nothing to see | Checks with a gap noted | Split / merge candidates
Electrical | 54 | 28 | 19 | 7 | 35 | 8 | 11 | 27 | 6
Mechanical | 113 | 85 | 25 | 3 | 49 | 61 | 3 | 67 | 30
Civil | 56 | 13 | 38 | 5 | 38 | 14 | 4 | 38 | 17
Building & Facilities | 38 | 14 | 19 | 5 | 31 | 5 | 2 | 14 | 2
Energy & Demand Management | 26 | 20 | 2 | 4 | 11 | 6 | 9 | 11 | 3
Process Safety & Risk | 37 | 20 | 11 | 6 | 20 | 12 | 5 | 24 | 7
ALL | 324 | 180 | 114 | 30 | 184 | 106 | 34 | 181 | 65

## Review
ID | Discipline | Asset system | Area | Requirement | Current vtype | Confirmed by | Go and see | Why that category | What to inspect | What makes it compliant | Gaps | Split / merge candidate
KSIA-ELE-001 | Electrical | AGL | AGL | All employees shall be trained and familiar with electrical safety and AGL with relevant certifications | Evidence + Site Physical Verification + Question | Document | reconcile | DoEL registered-person certificates matched to scope; the walk names who is actually on the AGL circuits and checks their expiry. | Identify who is currently working on or responsible for AGL circuits on site and cross-check their names, certificate expiry dates and scope against the registration and training records on file, including contractors and recent hires. | 1. Current DoEL registered-person certificates for each staff member working on AGL circuits, matched to scope. 2. Internal AGL/series-circuit training records (constant current regulators, isolating transformers, series-circuit safe working).
KSIA-ELE-002 | Electrical | AGL | AGL | Design and contruction shall be in accorandance to ICAO requirements and allow safe working for maintenance personnel | Evidence + Site Physical Verification | Document | examine | Approved as-builts referencing Annex 14 Ch.8; the walk confirms the designated isolation/maintenance points exist and are usable. | Locate the designated isolation/maintenance-access points on the AGL series circuit and confirm they exist and are usable; compare against the as-built drawings for any undocumented modifications. | Approved AGL electrical design drawings/as-built records referencing Annex 14 Ch.8 and Doc 9157 Part 5, showing de-energised isolation/maintenance-access points on the series circuits.
KSIA-ELE-003 | Electrical | AGL | AGL | Ensure a COC is issued by a competent, qualified and registered person | Evidence + Site Physical Verification | Document | examine | An original signed CoC, not a reprint; the walk finds alterations since its date not covered by a supplementary. | Walk the installation and check for any visible alterations or extensions since the CoC date that are not covered by a supplementary CoC. | Original, signed CoC for the AGL electrical installation (not a photocopy/reprint), plus any supplementary CoC covering later alterations.
KSIA-ELE-004 | Electrical | AGL | AGL | All statutory notices and signs should be clearly displayed | Site Physical Verification | Asset | examine | Signage present, legible and SANS 1186-1 compliant in every AGL room and outstation cabinet. Nothing documentary settles it. | Walk each AGL electrical room/work point, including remote outstation cabinets, and visually confirm statutory notices and SANS 1186-1 compliant signage are present, legible, not faded/damaged, and reference current appointees/policy revisions. | Statutory notices and SANS 1186-1 signage present, legible and undamaged at every AGL electrical room and remote outstation cabinet, naming the CURRENT appointees and policy revision — a notice carrying a departed GMR 2(1) appointee is not a notice. Checked daily per D060 023M cl. 4.7.4, warning signage weekly, with the substation logbook signed off. | NO evidence stated
KSIA-ELE-005 | Electrical | AGL | AGL | Ensure all associated regulary checks and functional tests are in place and performed | Evidence + Site Physical Verification | Practice | none | Gaps in the daily log over weekends, and entries batched afterwards rather than signed at the time. The log's EXISTENCE is not the test. | — nothing to inspect on site | Daily AGL serviceability inspection logs and weekly/monthly functional/electrical test reports for the full audit period.
KSIA-ELE-006 | Electrical | AGL | AGL | Check the degree of abnormality from baseline performance (all systems) through Light output, insulation resistance, PAPI angles | Evidence + Question | Document | none | Measured changeover time against the Annex 14 limit for the facility's category. | — nothing to inspect on site | 1. Monthly on-load changeover test record, with measured switch-over time compared against the Annex 14 limit for the facility's category. 2. Current flight-check/calibration report showing PAPI angle results, from the current audit cycle. 3. AGL insulation-resistance test log for runway/taxiway edge and PAPI circuits, with recorded megohm readings (not just pass/fail). | the row's own question asks what the aerodrome's certified lighting category IS — the limit cannot be applied without it
KSIA-ELE-007 | Electrical | AGL | AGL | Check lamp failure rate and spares holding | Evidence + Site Physical Verification | Document | examine | Fault log and spares register against the serviceability target; the walk counts spares against the lamp types actually in use. | Check the current lamp-fault log distinguishes critical lights from general edge lighting; physically check spares stock against lamp types in use and against the recent replacement log to see whether restorations were actually prompt. | ACSA's internal AGL serviceability target/procedure; recent lamp-fault/replacement log; current spares stock register.
KSIA-ELE-008 | Electrical | AGL | AGL | Ensure an active refurbishment/replacement plans are in accordance to the classification of assets | Evidence + Site Physical Verification + Question | Document | examine | A funded plan classifying assets by criticality; the walk spot-checks older assets against what the plan says should have happened by now. | Spot-check a sample of older/critical AGL assets on site against what the plan says should have happened to them by now. | ACSA's internal AGL asset management/life-cycle refurbishment plan, showing assets classified by criticality/age, with evidence of budget approval/scheduling.
KSIA-ELE-009 | Electrical | AGL | Serviceability | AGL photometric/serviceability inspections, lamp outage within limits, secondary power switch-over verified; CCR maintenance. | Evidence + Site Physical Verification + Question | Asset | examine | Lamp outage within limits is settled on the runway, ideally at night. | 1. Walk a sample section of runway/taxiway edge lighting (by day, or arrange a night inspection) and visually check lamp condition against the inspection log. 4. At the CCR room/enclosure, confirm regulators are present, correctly labelled, and show no visible signs of overheating, corrosion, or fault indication. | MALMS photometric output within limits and lamp outage inside the allowed count for the pattern, the Planned AGL Maintenance Programme M&E 077 worked to date, and the secondary-power switch-over measured at 1 second for every CAT II/III element (inner 300 m approach, threshold, end, centreline, touchdown zone) on the monthly on-load test with the change-over time actually recorded. | evidence stub: 'Inspection & test records' | photometric inspection, outage limits, switch-over and CCR maintenance are four tests
KSIA-ELE-010 | Electrical | Electricity Distribution System | Electricity Distribution System | Cable Arrangement, trenching, Handling shall be observed to SANS 10198 Arrangement of electric apparatus must afford accessibility to each part as needed to facilitate proper inspection, adjustment, maintenance, or replacement (Both within and outside). | Site Physical Verification | Asset | examine | Route markers matching the buried route, joint boxes not paved over, accessibility to each part. | Walk the cable routes and check route markers are present and match the actual buried route; locate joint boxes and confirm they are not paved or backfilled over; check the physical separation distance from other services (water, comms). | Cable routes to SANS 10198 with route markers present and matching the buried route, joint boxes not paved or backfilled over, the separation distances the standard requires actually measured on site, and every part reachable for inspection and replacement without dismantling something else. Commissioning test records for new MV/LV cabling and the as-built single line diagram behind it. | NO evidence stated
KSIA-ELE-011 | Electrical | Electricity Distribution System | Documentation | Current single-line diagrams displayed in each switch room; protection grading/settings study available and applied. | Evidence + Site Physical Verification + Question | Asset | examine | The requirement is that the diagram is DISPLAYED in the room — a physical fact. | 1. Walk each switch room and confirm a single-line diagram is physically displayed and legible; check its revision date against the most recent known network change. 2. Ask an ACSA electrician to show the settings on a sample protection relay and compare them to the values in the grading study. | A single-line diagram physically displayed and legible in EACH switch room, its revision date later than the most recent network change and reflecting the current Normal Open Point, plus a protection grading study whose settings an electrician can show applied in the relays — confirmed against design yearly with outage. | evidence stub: 'Drawings; protection study' | a displayed diagram (Asset) and an applied protection grading study (Document) are different tests
KSIA-ELE-012 | Electrical | Electricity Distribution System | Cable infrastructure | HV/MV cable routes marked, trenches/covers intact, cable test and thermography records; no unauthorised joints. | Evidence + Site Physical Verification | Asset | examine | Markers intact and not paved over; signs of unauthorised joints. | 1. Walk the accessible cable route markers and trench covers, checking they are intact, not paved over, and match the route drawing; look for any sign of unmarked excavation or an unrecorded joint. 2. Check the thermography survey date is within the applicable testing period and confirm any flagged hot spot has a documented repair. | Route markers and trench covers intact, not paved over and matching the route drawing; no unrecorded joint and no sign of unmarked excavation; and the yearly thermographic scan of bus bars, breaker frames, contacts, arc-chutes and insulation blocks with every flagged hot spot carrying a closed work order. | evidence stub: 'Cable records; inspection' | route condition (Asset) and thermography/test records (Document)
KSIA-ELE-013 | Electrical | Electricity Distribution System | Network configuration | No abnormal network configurations or equipment operating beyond design rating (kick-off risk item 6.5.1). | Evidence + Site Physical Verification | Asset | examine | Compare the single-line diagram against actual breaker positions. An abnormal configuration is a state, not a record. | Compare the single-line diagram against the actual switch/breaker positions to confirm the network is in its normal configuration; where load meters or ammeters are fitted, note the readings against equipment nameplate ratings. | Switch and breaker positions on site matching the Normal Open Point on the single-line diagram, no equipment carrying load above its nameplate rating, and the measured values inside ACSA's stated limits — power factor at least 0.95 at the point of delivery, 50 Hz ±2.5%, MV volt drop ±5%. This is kick-off risk item 6.5.1 and an abnormal configuration left standing is the finding. | evidence stub: 'Load readings; SLD verification'
KSIA-ELE-014 | Electrical | Switchgear | Switchgear | Yearly Functional Testing (SF6 /Vacuum) Certificate Yearly Continuity Test Certificate Yearly Contact Resistance Test Certificate Yearly Circuit Breaker Speed Test Certificate | Evidence + Site Physical Verification | Document | reconcile | Four certificates within 12 months per breaker, showing measured values against OEM tolerance; the walk reads the serial to prove they are THIS breaker's. | Locate each breaker's serial number/asset tag and match it to its four certificates; confirm certificate dates are within 12 months and show measured values against OEM tolerance rather than a pass tick. | Current (within 12 months) SF6/vacuum functional, continuity, contact resistance, and speed/timing test certificates per MV breaker, each showing measured values (not a bare pass/fail) and referencing the breaker serial number physically installed.
KSIA-ELE-015 | Electrical | Switchgear | Maintenance records | Annual switchgear maintenance report evidences ALL required checks: VCB service & timing, protection relay secondary-injection tests, auxiliary relays, panel/busbar inspection, insulation resistance, contact resistance. | Evidence + Site Physical Verification + Question | Document | reconcile | A signed report showing actual results for all six checks, not a checklist of ticks. | Pick a sample switchboard, note its serial/asset number, and match it to its maintenance report; check the report shows actual results for all six checks; look for a physical sign the board was actually opened and serviced around the report date (service sticker, tamper seal broken and replaced, fresh grease on moving parts). | Signed maintenance reports (last 12 months) per switchboard
KSIA-ELE-016 | Electrical | Switchgear | Condition & lifecycle | MV switchgear age/condition assessed; refurbishment or replacement plan in place for units beyond design life (>25-30 yrs) or with obsolete spares. | Evidence + Site Physical Verification | Document | examine | Condition assessment and a capital plan entry; the walk reads the nameplate date and looks for degraded condition. | Check the nameplate/manufacture date on a sample of switchgear units against the condition assessment; look for visible wear, corrosion, or degraded control wiring consistent with age, and check whether that unit appears on the refurbishment plan if it looks due. | Condition assessment report; capital plan entry
KSIA-ELE-017 | Electrical | Switchgear | Safe operation | Switching procedures, authorised persons (switching authority) register, arc-flash PPE and lock-out/tag-out available and used. | Evidence + Site Physical Verification + Question | Practice | examine | 'Available AND USED' is the requirement. Tests whether the register is maintained when someone leaves and whether LOTO is actually applied. | 1. Cross-check a name on the switching-authority register against staff actually present or working on switchgear. 2. Physically inspect arc-flash PPE (suits, visors, gloves) for condition and in-date inspection tags; check LOTO padlocks and permits are on hand and show signs of actual use, not just stored unused. | Authorisation register; procedures; PPE inspection | evidence stub | switching authority (Practice) and arc-flash PPE condition (Asset) in one row
KSIA-ELE-018 | Electrical | Substations | Substations | Dedicated electrical rooms for MV breaker, Transformer, LV Room, Generator Room and Battery room/UPS) | Site Physical Verification | Asset | examine | Rooms physically separate, each with its own access control rather than a shared key across risk classes. | Walk each room and confirm it is physically separate from the others, has its own access control (not a shared key/card across risk classes), and contains only its designated equipment (no incompatible storage, e.g. flammables in the battery room, or generator/battery rooms combined). | MV breaker, transformer, LV, generator and battery/UPS rooms each physically separate, each with its own access control rather than a shared key across risk classes, each containing only its designated equipment, oil-filled units with containment and fire-sealed penetrations. NOTE: ACSA states no numeric fire rating and no bund percentage for these rooms, so the compliance test is separation and containment as built, against the layout drawing. | NO evidence stated
KSIA-ELE-019 | Electrical | Substations | Substations | Rooms have adeqaute vetilation & cooling, fire protected, Roden free, Corrosion protected/free, drainage outlets | Evidence + Site Physical Verification | Asset | examine | Ventilation actually running rather than merely installed; rodent and corrosion free; drainage present. | In each electrical plant room, confirm ventilation fans/cooling are actually running (not just installed); check the fire-suppression certificate date; visually inspect for rodent droppings/nesting in cable trays or under raised flooring, corrosion on busbars/cable trays, and functioning floor drains. | Current fire-suppression system service/inspection certificate.
KSIA-ELE-020 | Electrical | Substations | Substations | Clear accesss and spacing shall be observed for all electrical equipment | Site Physical Verification | Asset | examine | Measure the clearance around switchgear and busbars against the NRS 060 table. A tape measure decides it. | Measure clearance distances around MV/LV switchgear and busbars on site and compare against the NRS 060 clearance table for the installed voltage class; check for storage or clutter encroaching into the clearance zone, and for any added equipment/trunking that may have reduced clearances since installation. | Clearance around MV/LV switchgear and busbars measured on site and at or above the NRS 060 figure for the installed voltage class, no storage or clutter inside it, doors serviceable, lockable and unobstructed, and exactly one door or gate left unlocked for emergency egress while work is in progress. | NO evidence stated
KSIA-ELE-021 | Electrical | Substations | Substations | Existence and adherence to Emergency plans | Evidence + Site Physical Verification | Document | examine | A plan that references the actual rooms on site rather than a generic site-wide document, plus drill records. | Confirm the plan references the actual electrical rooms/plant on site, not just a generic site-wide document; check evacuation routes/assembly points named in the plan still match the current site layout. | Current written emergency response plan covering electrical incidents; drill/training attendance records for the audit period.
KSIA-ELE-022 | Electrical | Substations | Substations | The latest revision of the substation diagram should be displayed at all times | Site Physical Verification | Asset | examine | Displayed at all times, legible, revision-dated. A physical fact about a wall. | Check the diagram is physically displayed, legible, and dated/revision-numbered; spot-check it against the actual switching configuration during the site walkdown for any recent changes not reflected on it. | The latest revision of the substation diagram displayed, legible, dated and revision-numbered, reflecting the current Normal Open Point, and matching the switching configuration found during the walkdown. Inspected daily with corrective action raised where it is out of date. | NO evidence stated
KSIA-ELE-023 | Electrical | Substations | Room condition | Access control, statutory signage, ventilation/HVAC functional, housekeeping, no unrelated storage, separation of MV/LV/UPS/CCR where practical. | Evidence + Site Physical Verification | Asset | examine | Door not propped open, signage legible, HVAC running, no unrelated storage. | Walk the substation and check the door is access-controlled (not propped open, not on a shared master key); confirm statutory signage is present and legible; check whether ventilation is actually running; look for unrelated items stored in the room; note whether MV, LV, UPS and CCR equipment are kept separate or crowded together. | Door access-controlled and not propped, keys issued through the key register with receipt on return, statutory signage present and legible, ventilation actually running, no unrelated storage, and MV/LV/UPS/CCR separated where practical — with the substation logbook showing all sixteen daily checks signed off. | evidence stub: 'Site inspection'
KSIA-ELE-024 | Electrical | Substations | Condition monitoring | Thermographic survey, earthing resistance and transformer oil (DGA/BDV) test records within period. | Evidence + Site Physical Verification | Document | examine | Thermography, earthing resistance and oil test reports within period; the walk looks for discolouration and melted insulation. | 1. Ask when the survey was last done and whether any flagged hot spot is now fixed; visually check for obvious overheating (discolouration, melted insulation) as a supporting check. 2. Locate the earth pit/test point and confirm it is accessible and carries a recent test tag. 3. Visually check the transformer's oil level gauge and look for leaks as a supporting check (the lab result itself is verified via the certificate). | Thermographic survey within the year with every hot spot closed out; earth resistance measured and recorded at the yearly transformer major maintenance; and transformer oil DGA/BDV within period with PCB content not more than 20 mg/kg in reclaimed oil and undetectable in unused oil, determined per IEC 61619 to SANS 555. NOTE: ACSA states no numeric earth resistance value, so the test is that a measured figure exists and is trended, against the design value. | evidence stub: 'Test reports'
KSIA-ELE-025 | Electrical | Generators | Generators | Functional test records - Monthly (AGL related) and yearly (all) | Evidence + Site Physical Verification + Question | Practice | none | The question is decisive: a complete log of tests that were START-AND-IDLE rather than ON-LOAD is a complete record of the wrong test. | — nothing to inspect on site | 1. Monthly on-load test/run logs for AGL-critical standby generators, covering the full audit period. 2. Annual test certificates for all other standby generators, covering the full audit period.
KSIA-ELE-026 | Electrical | Generators | Generators | Pressure test results for Underground fuel network | Evidence + Question | Document | none | A pressure/leak integrity certificate for the underground pipework. | — nothing to inspect on site | Current pressure/leak integrity test certificate for the underground fuel pipework; the internal ACSA procedure specifying the required test method and frequency. | the row's own question asks whether leak detection is by actual pressure test or only consumption reconciliation — those are different assurances
KSIA-ELE-027 | Electrical | Generators | Generators | Demarcation of Noise Zones and requirements for hearing protection | Evidence + Site Physical Verification | Asset | examine | Signage present and legible in the zones the assessment identifies, specifying the right protection. | Walk the plant areas identified in the noise assessment as noise zones and check signage is present, legible, and correctly specifies the hearing protection required; check any area added/changed since the last assessment has since been signed. | AIA (acoustic) noise assessment identifying areas at/above the 85 dB(A) action level.
KSIA-ELE-028 | Electrical | Generators | Generators | Declaration on MHI for Storage of explosives | Evidence + Site Physical Verification + Question | Document | reconcile | MHI declaration or written confirmation of being below threshold; the walk confirms the tank capacity matches the volume assessed. | 1. Confirm the physical tank capacity on site matches the volume used in any MHI assessment. 2. Confirm whether any explosives storage exists on site at all; where it does, check the physical storage against the licence conditions. | 1. ACSA's MHI risk assessment/declaration status for the site, or written confirmation storage volumes fall below MHI thresholds. 2. Any Explosives Act licence/declaration, if explosives distinct from diesel fuel are stored.
KSIA-ELE-029 | Electrical | Generators | Generators | Requirement to not expose personnel to >85dBA subject to regulation 9 and 10(1) | Evidence + Site Physical Verification | Practice | examine | Whether staff entering the generator room during operation ACTUALLY wear the issued protection. Issue records prove issue, not use. | Spot-check whether staff entering generator rooms during operation are actually wearing issued hearing protection; check the noise exposure assessment measures duration of exposure, not just sound level; confirm regularly-exposed employees appear on the audiometric enrolment list. | Noise exposure assessment for generator operating/maintenance areas showing 8-hour TWA readings; audiometric/hearing-conservation programme enrolment records; hearing protection issue records.
KSIA-ELE-030 | Electrical | Generators | Fire safety | Diesel supply to each generator fitted with an accessible fire cut-out / isolation device (fusible-link valve or cut-out) and emergency stop; clearly labelled. | Evidence + Site Physical Verification + Question | Asset | examine | The cut-out and e-stop located, labelled, unobstructed. A March 2025 Unacceptable finding sat here. | At each generator, physically locate the fuel cut-out/isolation device and the emergency stop button; confirm both are clearly labelled, unobstructed, and reachable without approaching the generator itself during a fire; check the cut-out is not painted over, rusted shut, or blocked. | A fuel cut-out or isolation device and an emergency stop at each generator, both clearly labelled, unobstructed and reachable WITHOUT approaching the generator itself, with the fuel line shut-off valve checked to operate freely weekly and the stop solenoid checked on the monthly record. | evidence stub: "Physical inspection; drawings"
KSIA-ELE-031 | Electrical | Generators | Testing | Weekly no-load / monthly on-load test records and annual load-bank test; fuel consumption & run-hours logged. | Evidence + Site Physical Verification | Document | reconcile | Weekly/monthly entries without gaps and an annual load-bank test; the walk compares the hour-meter to what is logged. | Check a generator's logbook on site for gaps in the weekly/monthly entries; check the hour-meter reading roughly matches what's logged; ask when the last annual load-bank test was done and for which generator, and ask to see that certificate. | Weekly off-load runs of at least five minutes and monthly on-load runs of at least fifteen minutes, with no gaps in the logbook, the hour-meter reading consistent with what is logged, the change-over time recorded on each on-load test, and an annual load-bank test plus fuel sample analysis for every generator — not just the main one. | evidence stub: 'Generator test logs'
KSIA-ELE-032 | Electrical | Generators | Change-over | Automatic transfer (ATS) tested; switch-over time within design for AGL/critical loads. | Evidence + Site Physical Verification | Document | examine | ATS test records showing switch-over within design; the walk finds a recent test or service tag on the cabinet. | Locate the ATS cabinet/panel and check for a recent test or service tag; if a routine test can be safely observed or a recent test log/video reviewed, confirm the recorded changeover time. | A tested ATS with the measured change-over time at or under the design figure for the load it feeds — 1 second for every CAT II/III AGL element. A test record with no time on it does not answer this check. | evidence stub: 'ATS test records'
KSIA-ELE-033 | Electrical | Generators | Fuel storage | Day/bulk tank bunded, level alarms functional, spill kit available, fuel polishing/quality tests, no leaks. | Evidence + Site Physical Verification | Asset | examine | Bund cracked or full of rainwater, spill kit missing, visible leaks. | 1. Inspect the bund wall for cracks or damage, and check it isn't full of rainwater (reducing spill capacity); locate the spill kit and check it's stocked and accessible; check for any sign of a fuel leak around the tank and pipework. 2. Check the fuel test/polishing certificate date against the site's stated testing interval. | Bund intact, not cracked and not full of rainwater (which is capacity gone), sized to at least 110% of the largest container, level alarms proven on the weekly alarm check, a stocked and accessible spill kit, no leaks or staining, and the annual bulk-tank bottom and primary-filter samples analysed for contamination. | evidence stub | bund condition and alarms (Asset) vs fuel quality tests (Document)
KSIA-ELE-034 | Electrical | Transformers | Transformers | Check the degree of abnormality from baseline performance | Evidence + Question | Document | none | Current-year oil report with prior years for trending. | — nothing to inspect on site | Current-year transformer oil test report (BDV, moisture, acidity, DGA where available) and prior years' results for trending. | the row's own question asks whether DGA was actually done or only basic tests — a different assurance
KSIA-ELE-035 | Electrical | Transformers | Maintenance | Transformer inspection: oil level/leaks, silica gel, bushings, cooling, protection (Buchholz/temperature) tested; nameplate & loading within rating. | Evidence + Site Physical Verification | Asset | examine | Oil level, leaks and staining, silica gel colour, bushings, cooling fins. All read at the transformer. | 1. At the transformer, check the oil level gauge, look for leaks or staining, check silica gel colour, and inspect bushings and cooling fins/radiators for damage or contamination. 2. Check the nameplate rating (kVA) and, if a load reading is available on site, compare it against the rating. | Oil level in band with no leaks or staining, silica gel the right colour, bushings and cooling fins undamaged and clean, Buchholz and temperature protection warning and trip functionality tested at the yearly major maintenance with outage, and the measured loading inside the nameplate rating. | evidence stub: 'Inspection records'
KSIA-ELE-036 | Electrical | UPS | Performance | Battery impedance/capacity tests, autonomy (discharge) test, alarms monitored, room temperature within battery spec. | Evidence + Site Physical Verification + Question | Document | examine | Impedance/capacity and discharge test certificates — a discharge test is verified by certificate, not observed; the walk looks for swelling, leakage, corrosion. | 1. Visually inspect battery cabinets for swelling, leakage, or corrosion (a discharge test itself is verified via the certificate, not observed live). 2. Check the monitoring panel/display on site is live and showing current status, not faulted or blank. 3. Check the room's thermometer or data-logger reading against 25°C at the time of the walkabout. | Battery impedance or capacity results and a full-duration autonomy discharge test within period, alarms proven to reach the monitoring point, and the UPS room temperature inside the battery manufacturer's specification — recorded on the annual service alongside cell readings, charger voltage, inverter output and the bypass switch test. | evidence stub
KSIA-ELE-037 | Electrical | ILS | ILS | Calibration records (bi-annual) | Evidence + Site Physical Verification | Document | none | The flight-check report itself, within the facility's interval — not ground maintenance records standing in for it. | — nothing to inspect on site | Current ILS flight calibration report (within the facility's stated interval), with course alignment, glide path angle and signal clearance results within Annex 10 tolerances for the facility's ILS category.
KSIA-ELE-038 | Electrical | ILS | ILS | is there a significant deviation beyond strict limits? | Evidence | Document | none | Each parameter against the Annex 10 tolerance table for the facility's category. | — nothing to inspect on site | Latest ILS calibration report with each parameter compared against the Annex 10 tolerance table for the facility's category; any NOTAM/corrective-action record for out-of-tolerance results.
KSIA-ELE-039 | Electrical | AWOS | AWOS | AWOS calibration | Evidence + Site Physical Verification | Document | reconcile | Calibration certificates per sensor within validity; the walk reads each sensor's tag date against its certificate. | Check the calibration sticker/tag date on each sensor (wind, RVR/visibility transmissometer, cloud base, temperature/pressure) against its certificate; check whether some sensors are current while others are overdue. | Current calibration certificates for each AWOS sensor, issued by SAWS or an accredited provider and within stated validity; ACSA/ATNS's internal AWOS maintenance procedure specifying the required interval.
KSIA-ELE-040 | Electrical | Lighting | Lighting | The lighting level of the main lighting shall be measured to ensure complaince for intended use | Evidence + Site Physical Verification | Document | none | A lux survey measured at the actual task points, within the two-year re-survey interval. | — nothing to inspect on site | Current lux-meter survey report for each relevant area (electrical rooms, plant rooms, workstations), compared against the Schedule minimum for that task.
KSIA-ELE-041 | Electrical | Lighting | Apron & landside | Apron floodlighting levels and uniformity, high-mast structures inspected, landside/parking lighting operational. | Evidence + Site Physical Verification | Asset | examine | Dark or uneven apron areas at night, and high-mast base/foundation condition. | 1. Visually assess apron lighting, ideally at night, for obviously dark or uneven areas as a supporting check. 2. Visually inspect the base/foundation of a sample high-mast for corrosion, cracking, or leaning, and check the fixings and access ladder condition. 3. Walk or drive through the landside/parking areas, ideally at night, and note any non-working fittings. | Measured lux readings on the specified grid at or above 20 LUX per ICAO Annex 14 §5.3.24, taken monthly, with uniformity across the apron rather than an average that hides a dark stand; high-mast structures and foundations inspected for corrosion and cracking; landside and parking lighting operational. | evidence stub: 'Lux measurements; inspection'
KSIA-ELE-042 | Electrical | Emergency Lighting | Testing | Emergency and escape-route lighting monthly function tests and annual full-duration tests logged. | Evidence + Site Physical Verification | Document | examine | Monthly function and annual full-duration tests logged; the walk actually isolates a fitting to see it switch on. | Test, or ask ACSA to test, a sample emergency/escape-route light fitting by briefly isolating its local supply to confirm it switches on; check fittings are undamaged and unobstructed; check the test register is signed for the current month. | Monthly function tests and an annual full-duration test logged per fitting, six-monthly integrity testing of the back-up supply with a light output measurement, daily escape-route clearance checks, and fittings found undamaged and unobstructed on the walk. | evidence stub: 'Test register'
KSIA-ELE-043 | Electrical | FDS & Gaseous Suppression | Servicing | Fire detection system serviced and certified; quarterly functional tests; gaseous suppression cylinder pressure/weight checks and room-integrity test. | Evidence + Site Physical Verification | Document | examine | Service certificates and quarterly test logs; the walk reads the panel for faults and the cylinder gauges. | 1. Check the fire panel for fault/service indicator lights and confirm the service sticker/tag date. 2. Physically inspect suppression cylinder pressure gauges (should read normal/green) and check the weight-check tag date; check the protected room's door seals and any wall/floor/ceiling penetrations look properly sealed. | Fire detection inspected weekly and maintained monthly with the panel showing no standing fault, quarterly functional tests logged, gas suppression maintained yearly with each cylinder's weight, gas type, inspection date and next service recorded, cylinders within their 10-yearly hydrostatic test, and a room-integrity (door fan) test proving the enclosure will hold the concentration. | evidence stub | detection servicing, suppression cylinder checks and room-integrity testing are three tests
KSIA-ELE-044 | Electrical | X-Ray Machines | Radiation control | Radiation licence/registration current, Radiation Protection Officer appointed, leakage/dose surveys and service records available. | Evidence + Site Physical Verification | Document | reconcile | Licence current and matching the machine's serial; RPO appointed. | At each X-ray machine, check the licence/registration is available and matches the machine's serial number; ask staff who the appointed RPO is and check it matches the appointment record; check for a current service sticker/tag. | Current Department of Health radiation registration verified annually and matching each machine's serial number, an appointed Radiation Protection Officer whom staff can name and whose appointment record matches, tri-monthly leakage survey and calibration certificates, and deregistration records for any machine removed. | evidence stub: 'Licence; survey reports'
KSIA-ELE-045 | Electrical | Earthing & Lightning Protection | Testing | Earthing and lightning-protection systems tested and records within period; bonding of airside structures/fuelling points. | Evidence + Site Physical Verification | Document | examine | Test certificates within period; the walk checks bonding cables at a fuelling point are intact and not corroded or disconnected. | At a sample structure or fuelling point, check the earthing/bonding cable and connection points are physically intact, not corroded or disconnected; check for a test tag showing a recent date; visually inspect lightning air terminals/down-conductors on tall structures for damage. | Earth resistance and lightning-protection test certificates within period, and bonding at airside structures and fuelling points physically intact, uncorroded and connected with a test tag showing a recent date. NOTE: ACSA states no numeric ohm value, so the test is a measured figure against the design value and its trend — not the absence of one. | evidence stub: 'Test certificates'
KSIA-ELE-046 | Electrical | General Electrical Installation | General Electrical Installation | All employees shall be trained and familiar with electrical safety and circuitry | Evidence + Site Physical Verification + Question | Document | reconcile | Training records and DoEL registration; the walk asks staff what training they had and cross-checks the register. | 1. Ask staff working near electrical circuitry what electrical hazard training they've had and when; cross-check against the training register. 2. Identify anyone on site performing electrical installation work, including contractors, and confirm their DoEL registration certificate is on file and was actually checked. | 1. Electrical safety induction/training records for staff working near circuitry. 2. Current DoEL registration certificates for anyone (including contractors) performing fixed-installation electrical work.
KSIA-ELE-047 | Electrical | General Electrical Installation | General Electrical Installation | Design and construction of electrical installation to be according to SANS 10142 as incorporated under section 44 of ACT | Evidence + Site Physical Verification | Document | examine | As-builts and CoCs referencing the SANS 10142-1 edition current when the work was done; the walk finds undocumented changes. | Compare as-built drawings against the physical installation for undocumented changes; check any recent work or alterations has its own fresh CoC covering the altered portion. | As-built drawings and CoCs for LV installations, confirming reference to SANS 10142-1 and the edition current at the time the work was done.
KSIA-ELE-048 | Electrical | General Electrical Installation | General Electrical Installation | All statutory notices and signs should be clearly displayed | Site Physical Verification | Asset | examine | Notices present, legible, not faded or damaged, at each electrical room and work point. | Walk each electrical room/work point and visually confirm statutory notices and SANS 1186-1 compliant signage are present, legible, not faded/damaged, and reference current appointees/policy revisions. | As ELE-004, across every general electrical room and work point: statutory notices, SANS 1186-1 signage, circuit labels and legend cards present, legible and current, checked daily, warning signs and safety devices confirmed present and correctly positioned. | NO evidence stated
KSIA-ELE-049 | Electrical | General Electrical Installation | General Electrical Installation | Ensure all associated regulary checks and functional tests are in place and performed | Evidence + Site Physical Verification | Practice | none | As ELE-005 for the general installation: gaps in the log and batched sign-off are the finding. | — nothing to inspect on site | Daily serviceability inspection logs and weekly/monthly functional/electrical test reports for the full audit period.
KSIA-ELE-050 | Electrical | General Electrical Installation | General Electrical Installation | Protection against direct contact shall be observed | Evidence + Site Physical Verification | Asset | examine | Enclosure panels left open or unlocked after maintenance; barrier voltage ratings against the installed class. | 1. Physically inspect enclosure panels for any left open or unlocked after maintenance; check the voltage rating marked on each barrier/enclosure against what is actually installed behind it. 2. Cross-check the ORHVS-authorised persons register against current staff records for anyone listed who is no longer employed or authorised. | ORHVS-authorised persons register for anyone accessing HV/MV areas.
KSIA-ELE-051 | Electrical | General Electrical Installation | General Electrical Installation | Isolation and lockout requirements including earthing requirements for machinery that can acquire electrical charge. Check that distribution panels can be isolated and locked out | Evidence + Site Physical Verification + Question | Practice | examine | The question is the test — is LOTO bypassed 'for a quick job'. Lockable isolators existing is necessary and not sufficient. | Physically test/observe that distribution panels/switchboards have lockable isolators; check padlocks and permits are actually being issued and used, not just available; check earthing/discharge equipment is present. | Site's documented LOTO procedure; padlock/permit register; earthing/discharge equipment test/inspection record for MV/HV work.
KSIA-ELE-052 | Electrical | General Electrical Installation | General Electrical Installation | Safe Work Method Statements and records | Evidence + Question | Practice | none | Whether each SWMS is specific to the job's hazards or one generic document reused. A file full of identical SWMSs passes a document test and fails this one. | — nothing to inspect on site | Safe Work Method Statements/permit-to-work documents for higher-risk electrical tasks performed during the audit period, with worker sign-off dated before the task began.
KSIA-ELE-053 | Electrical | Electrically Driven Machinery | Electrically Driven Machinery | Functional test records - Yearly | Evidence + Site Physical Verification | Document | none | A current GMR 2.1 appointment naming someone still on the roster, plus a dated functional test log. | — nothing to inspect on site | 1. Written, signed GMR 2.1 appointment letter, current and naming someone still on site. 2. Functional/inspection test log for the driven machinery, covering the full audit period, each entry dated, signed and showing actual results.
KSIA-ELE-054 | Electrical | Electrically Driven Machinery | Electrically Driven Machinery | Requirements to safe guard machinery and ensure they are installed, operated and maintained in a manner to prevent exposure to hazards | Evidence + Site Physical Verification | Asset | examine | Guards fitted over rotating parts and live terminals, not removed or propped open. | Physically inspect the machine for guards fitted over all rotating/moving parts and live terminals; check guards are not removed, propped open, or have interlocks defeated. | Machine-specific risk assessment identifying residual hazards and controls (not a generic site-wide document).
KSIA-MEC-001 | Mechanical | HVAC | HVAC | Flow test records of Fresh air induction Fans | Evidence + Site Physical Verification | Document | reconcile | A measured L/s per person on a dated test report. The walk only proves the fan is running and that the space is the space that was tested. | Locate the fresh-air induction fan(s) serving the space, confirm they are running, and check whether the space's actual use (terminal concourse vs office) matches the classification used in the test report — a mismatch (e.g. an office rate applied to a public concourse) is a fail. | Independent air-flow test for the space, measured fresh-air rate against the >7.5 L/s/person target, with the space classified as it is actually used — an office re-let as a concourse invalidates the report. | ACSA requires only a six-monthly MOTOR RUNNING CURRENT — no air-flow rate, velocity or L/s figure anywhere in D080 025M. The check asks for a test ACSA's own manual does not call for.
KSIA-MEC-002 | Mechanical | HVAC | HVAC | Flow test records of Toilet extraction fans | Evidence + Site Physical Verification | Document | reconcile | Air changes per hour is a calculation from a measured extract rate and the room's real volume. Neither is visible. | With the door closed as in normal use, confirm the extract fan is running and audibly/visibly drawing air (e.g. a tissue-flutter check at the grille); check the report's room volume against the actual room, and check whether a known shortfall (e.g. 12 ACH) has a linked corrective-action record. | ACH report with the room volume used, the measured extract flow, and the calculated ACH — with the volume matching the actual room. | ACSA states no extraction rate or air-change requirement — only motor running current
KSIA-MEC-003 | Mechanical | HVAC | HVAC | Flow and functional test records of smoke extraction fans | Evidence + Site Physical Verification | Document | examine | The required extraction rate comes from the fire engineering design; only a commissioning certificate can show the fan achieves it. | Locate the smoke extraction fan and confirm it can be observed running; check whether the test was performed with the fan actually tied into a fire-alarm trigger (not standalone), and check the duct/fan configuration in the field against the design report, flagging any later works that changed the as-built layout. | Approved smoke control design stating the rate for the zone, plus a functional test certificate showing the fan reached it when triggered BY the fire alarm, not standalone. | ACSA's threshold is a 3-monthly auxiliary activation test, not a flow rate
KSIA-MEC-004 | Mechanical | HVAC | HVAC | Records of duct cleaning (Fat removal) | Evidence + Site Physical Verification + Question | Document | examine | Grease depth in a duct is the fact, and it is behind an access panel. The certificate says the run was cleaned; the panel says whether it was cleaned end to end. | Where accessible, visually inspect kitchen extract ductwork (or access panels) for grease/fat buildup; compare against the report's before/after photos or deposit-depth reading, and confirm cleaning covers the full duct run to the extract fan, not just accessible sections. | Deep-clean certificate per SANS 1850:2003 at an interval not exceeding six months, with before/after photographs or a deposit-depth reading covering the full duct run to the discharge point.
KSIA-MEC-005 | Mechanical | HVAC | HVAC | Functional test records of roof vents | Evidence + Site Physical Verification + Question | Document | reconcile | A seized vent is visible on the roof, but what fails this check is a blanket 'all vents OK' sign-off with no per-unit entry. | Access the roof (or a vantage point) and check a sample of roof vents for free rotation/operation and for seizure or corrosion; compare against the log's most recent per-unit entries — a blanket "all vents OK" sign-off with no per-unit detail is a red flag. | Monthly log with a per-unit reference and pass/fail, and a roof sample turning freely without seizure or corrosion. | no acsaThreshold — no monthly roof-vent test interval is stated anywhere in the source
KSIA-MEC-006 | Mechanical | HVAC | HVAC | Functional Test records of Fire dampers | Evidence + Site Physical Verification + Question | Document | reconcile | A damper closes or it does not, and only a functional test says so. The walk finds the ones painted over or sealed above a ceiling. | Select a sample of dampers from the register, physically locate them (checking access panels aren't sealed/obstructed above ceilings), and visually confirm none are painted over or obstructed such that they couldn't close; cross-check the sample against the full register to confirm no dampers are missing from testing. | Test record per damper reference showing full closure and reset, cross-referenced to the fire safety file — and a located sample with its access panel still openable and the blade not painted shut.
KSIA-MEC-007 | Mechanical | HVAC | HVAC | Certificate of Conformity for Refrigerant gas lines | Evidence + Site Physical Verification | Document | reconcile | A Certificate of Conformity under PER reg 17 is the only proof. The walk matches the plant-room reference on it to the pipework actually installed. | Physically trace the refrigerant gas line installation and check the CoC's plant room/asset references match what's actually installed; look for any visibly recent modification (new sections, welds, added branches) not reflected on the certificate. | Current CoC from an Approved Inspection Authority, and no unrecorded modification — new branches or welds — since its date.
KSIA-MEC-008 | Mechanical | HVAC | HVAC | Legionela test and clearance certificate | Evidence + Site Physical Verification | Document | reconcile | A Legionella result is a laboratory number. The walk exists to count towers, because a certificate for one tower on a site with three is the failure. | Physically locate each cooling tower/evaporative condenser on site and count them against the certificates held — a certificate covering only one tower when the site has several is a fail; check the certificate's sampling point description against the actual system. | A dated clearance certificate within 12 months for EACH water-cooled or evaporative system, with sampling points that match the plant on site. | no acsaThreshold at all — SANS 10147 cl. 6.1.6.1 is named in the evidence but no ACSA interval is quoted
KSIA-MEC-009 | Mechanical | HVAC | HVAC | COC for electrical reticulation in plant rooms | Evidence + Site Physical Verification | Document | reconcile | An EIR reg 6 Certificate of Compliance signed by a registered person. The walk looks for circuits added since. | Walk the plant room and visually compare the wiring/DB layout against what the CoC describes; look for obvious un-certified additions (new circuits, extensions) and check the registered person's details are stated on the CoC, not just an invoice. | Current CoC in the latest SANS 10142-1 format naming the registered person, matching the as-installed wiring with no un-certified additions.
KSIA-MEC-010 | Mechanical | HVAC | HVAC | Wiring diagrams | Evidence + Site Physical Verification | Document | reconcile | A drawing is compliant when it matches the installation, which is only knowable by tracing circuits against it. | In the plant room, physically trace a sample of circuits/panel labelling against the diagram; check the diagram carries a version/date. A diagram that is only the original design drawing (never updated), or held only centrally and not on site, is a fail. | Dated, version-controlled as-built set — 1 electronic and 3 hard copies per D100MAN cl. 9.2 — with panel labelling in the plant room matching it, not the original design issue never updated.
KSIA-MEC-011 | Mechanical | HVAC | HVAC | HVAC/FIRE Detection interface test records | Evidence + Site Physical Verification | Document | examine | An interface test is a record of a response that has already happened. What matters is whether the HVAC plant moved, or only the fire panel logged. | Where a live or simulated test can be reviewed on site, check that the HVAC equipment response was actually exercised (not the fire panel alone), and confirm a cause-and-effect matrix exists covering all interface zones, not just some tested each quarter. | Quarterly record showing the alarm triggered and the HVAC response observed, cross-referenced to a cause-and-effect matrix covering every interface zone.
KSIA-MEC-012 | Mechanical | HVAC | HVAC | DB Earth leakage | Evidence + Site Physical Verification | Document | reconcile | The trip current and time are on a drawing and in a test record. The walk reads the installed device's rating and looks for a bypass. | At the DB, check the installed ELU/RCD's rated current against the design drawing; check for evidence of an actual measured trip test (not just a test-button press), and check the unit hasn't been bypassed for nuisance tripping without reinstatement. | DB design/as-built drawing stating the specified earth-leakage trip current and time. Latest trip test record confirming the unit trips within that rating. | no standalone earth-leakage test interval in ACSA — it rides on the yearly COC cycle this identical check appears six times in the register: MEC-012, 052, 064, 087, 092, 102 | one earth-leakage check scoped by asset system, not six near-identical rows
KSIA-MEC-013 | Mechanical | HVAC | HVAC | Refrigerant leak test records | Evidence + Site Physical Verification + Question | Document | examine | A leak check is an event with a method. Repeated top-ups with no investigated cause is the finding, and it is only visible in the log. | At the refrigeration/AC plant, check the leak-check method actually used (visual vs electronic detection) is stated in the record; check refrigerant top-up logs for a pattern of repeated top-ups without an investigated cause, which would mask an ongoing leak. | Quarterly leak-check record per refrigerant circuit stating the detection method used and referenced to the charge, with any detected leak repaired and verified.
KSIA-MEC-014 | Mechanical | HVAC | HVAC | Indoor air quality measurements (Airport Environmental dept) | Evidence + Question | Document | none | A laboratory report from the Environmental department against stated guideline values. Nothing on site changes it. | — nothing to inspect on site | IAQ report within the two-year Occupational Hygiene cycle, naming the reference standard it was assessed against. | no walkabout text at all, correctly
KSIA-MEC-015 | Mechanical | HVAC | HVAC | Energy Optimisation functional audit | Evidence + Site Physical Verification | Document | reconcile | An audit report and its recommendations. The walk spot-checks whether a named finding was actually actioned. | Where the report cites a specific finding (e.g. a specific AHU or chiller flagged), spot-check that unit's current condition against the finding to confirm it was actually actioned. | Annual energy optimisation report for the HVAC plant, and for each cited finding either a closed work order or the unit visibly in the state the recommendation called for.
KSIA-MEC-016 | Mechanical | HVAC | HVAC | Noise monitoring requirement by an AIA according to SABS 083 | Evidence + Site Physical Verification | Document | reconcile | A SANS 10083 noise assessment by an Approved Inspection Authority. The walk checks the zones it named are demarcated on the ground. | Walk the plant rooms/noise areas named in the AIA report and check the noise-zone demarcation/signage on site matches what the report identifies; confirm the report covers the full facility, not only some plant rooms. | Current AIA occupational noise assessment report (SANS 10083 methodology), dated within the regulatory cycle. Identifies noise zones and any areas at/above the 85 dB(A) action level. | verbatim duplicate of MEC-105 — same requirement, evidence and walkabout, one filed under HVAC and one under Water Treatment Plant | one noise-survey check for the site; demarcation is separately MEC-104
KSIA-MEC-017 | Mechanical | HVAC | Plant operation | Chiller/AHU plant logs: set-points, ΔT, alarms cleared; controls in AUTO; refrigerant leak log; PER certificates for pressure equipment. | Evidence + Site Physical Verification | Document | reconcile | Weekly logged temperatures, pressures and amps against set-points. AUTO mode and an unacknowledged alarm are read off the BMS screen. | 1. At the plant room/BMS screen, check the controller mode is AUTO, look for any active or unacknowledged alarms, and note the current supply/return temperatures against the delta-T logged. 2. At the chiller, look for visible signs of refrigerant leakage such as oil staining at pipe joints or ice build-up on refrigerant lines, and check gauge pressures look normal. 3. Locate the pressure vessel nameplate on site and check its ID matches the PER certificate, and confirm the certificate's next-due date has not passed. | Weekly chiller records of temperature, pressure and amps with the delta-T against design, controller in AUTO with no standing alarm, yearly oil sample analysis and the safety-device test. | evidence stub: 'Plant logs; PER certificates' overlaps MEC-007 (PER certificates) and MEC-013 (refrigerant leak log) | keep the plant-log half; the PER certificate is MEC-007 and the leak log is MEC-013
KSIA-MEC-018 | Mechanical | HVAC | Legionella & water treatment | Cooling towers/evaporative condensers: water treatment programme, cleaning & disinfection records, Legionella testing. | Evidence + Site Physical Verification | Document | examine | The dosing regime and its test results decide it — but biological growth in the basin is visible and contradicts a clean record. | 1. At the cooling tower, check dosing pumps and chemical tanks are present, connected and appear to be operating — not empty or disconnected. 2. Physically inspect the cooling tower basin and fill for visible biological growth (slime, algae), scale build-up or debris. | A documented water treatment programme with dosing pumps and chemical tanks connected and charged (not empty or disconnected), cleaning and disinfection records, monthly leak/eliminator/fan/spray inspection and tri-monthly sump cleaning per the Cooling Towers checklist CMMS 009 — and a basin and fill free of visible biological growth, which contradicts a clean record. | evidence stub: 'Treatment & test records' overlaps MEC-008, whose evidence is the same Legionella certificates | keep the water-treatment programme and cleaning records here; Legionella testing is MEC-008
KSIA-MEC-019 | Mechanical | People Movers | People Movers | Annexure A certificates for Lifts/Elevators | Evidence + Site Physical Verification | Document | reconcile | An Annexure A is issued once, after erection. The walk matches the serial plate to the certificate and looks for a controller change that voids it. | At each lift, check the asset/serial number plate against the certificate on file; check for evidence of a substantial modification (e.g. a new controller) since the certificate date that would require a fresh Annexure A. | Annexure A per lift referencing SANS 1545-1 or 1545-2, with a fresh one after any substantial modification.
KSIA-MEC-020 | Mechanical | People Movers | People Movers | Validity of Annexure B certificates for Lifts/Elevators | Evidence + Site Physical Verification | Document | reconcile | A two-yearly thorough examination report with a next-due date. The walk's job is counting — every lift in a bank, not most of them. | At each lift bank, check that every lift has its own current Annexure B (not just some of a bank); check the certificate's "next examination due" date hasn't already passed. | Annexure B per lift dated within 24 months, examiner's registration stated, next-due date not yet passed.
KSIA-MEC-021 | Mechanical | People Movers | People Movers | Annexure A certificates for Escalators/Passenger conveyors | Evidence + Site Physical Verification | Document | reconcile | As MEC-019, for escalators and conveyors against SANS 1543. | At each escalator/conveyor, check the unit reference against the certificate; check for signs of modification since certification without a fresh Annexure A. | Annexure A certificate of test and examination after installation for each escalator/passenger conveyor. References SANS 1543. | ACSA's threshold here is a MONTHLY check of the reports, which is a different obligation from holding a valid Annexure A
KSIA-MEC-022 | Mechanical | People Movers | People Movers | Validity of Annexure B certificates for Escalators/Passenger conveyors | Evidence + Site Physical Verification | Document | reconcile | As MEC-020, for the escalator and conveyor fleet. | At the escalator/conveyor fleet, check every unit has its own current Annexure B, not only some of the fleet; check the certificate's next-due date hasn't passed. | Annexure B per unit dated within 24 months across the whole fleet, next-due date not passed.
KSIA-MEC-023 | Mechanical | People Movers | People Movers | Annex A - Certificate of tests and examination after Installation of Platform Stairlifts | Evidence + Site Physical Verification | Document | reconcile | A SANS 1545-3 certificate per stairlift. The walk finds the unit installed in an accessibility upgrade that nobody certificated. | Locate each platform stairlift, including any newer unit installed as part of an accessibility upgrade, and confirm each has its own certificate on file referencing SANS 1545-3, and that the installer/examiner is registered. | Annexure A certificate of tests and examination after installation, referencing SANS 1545-3, for each platform stairlift. | no acsaThreshold — platform stairlifts are not in D080 020M's inspection tables at all
KSIA-MEC-024 | Mechanical | People Movers | People Movers | Annex E - Comprehensive report of lifts for persons with disabilities | Evidence + Site Physical Verification + Question | Document | reconcile | An Annexure E must address accessibility features. A generic Annexure B filed under this heading is the failure, and only reading it shows that. | At each accessibility lift, check the report actually addresses accessibility-specific features (audible/tactile controls, door timing), not just a generic Annexure B; check the certificate hasn't lapsed. | Current Annexure E addressing audible and tactile controls, door timing, alarm button at 900-1200 mm and a mirror where the car is under 1 500 mm wide.
KSIA-MEC-025 | Mechanical | People Movers | People Movers | 6 monthly Lift Suspension Ropes' examination report | Evidence + Site Physical Verification | Document | reconcile | Rope discard criteria are applied by a competent person against a specific rope set. Visible corrosion in the hoistway supports or contradicts the report. | At the lift machine room/hoistway, visually inspect the suspension ropes for visible wear, broken wires or corrosion where accessible, and check the report identifies the specific rope set inspected rather than a generic "ropes OK"; if ropes were replaced, confirm a new examination report exists. | Six-monthly examination naming the specific rope set, assessed against discard criteria, with the certificate in its designated place in the machine compartment and retained ten years.
KSIA-MEC-026 | Mechanical | People Movers | People Movers | Annual Lift Safety gear, over speed governor and buffers examination report | Evidence + Site Physical Verification | Document | examine | A destructive test that has already happened; the report is all there is. What it must show is a measured trip speed, and all three elements tested. | Where a witnessed test or recent test evidence is available, confirm all three elements — safety gear, governor, and buffers — were actually tested (not just the governor), and that the report states a measured trip speed with units, not just "pass". | Annual report per lift confirming safety gear engaged, the governor tripped at a measured speed with units stated, and the buffers tested — not the governor alone.
KSIA-MEC-027 | Mechanical | People Movers | People Movers | Certificate of Compliance for an Electrical Installation | Evidence + Site Physical Verification | Document | reconcile | As MEC-009, for the lift motor room supply and control panel. | At the lift motor room/control panel, check the panel/asset reference on the CoC matches what's installed, and look for signs of a motor or controller replacement since the CoC date. | Current Certificate of Compliance for the lift/escalator plant's electrical installation (motor room supply, control panel), issued by a registered person. | duplicates the CoC pattern of MEC-009, 031, 052, 064, 089, 094, 101
KSIA-MEC-028 | Mechanical | People Movers | Statutory inspection | Lifts, escalators and travelators: annual inspection & comprehensive test by a registered Lift Inspector; register of lifts/escalators; certificates displayed. | Evidence + Site Physical Verification + Question | Document | reconcile | A roll-up of the certificate checks above, adding one thing they miss: whether the register lists every unit in the terminal. | 1. At a sample of units, check the displayed certificate is current (not expired) and matches the unit's ID. 2. Walk the terminal and identify all visible lifts, escalators and travelators, cross-checking against the register to confirm none are missing from it. 3. At each unit, physically check whether a certificate is displayed and whether its expiry date has passed. | A register listing every lift, escalator and travelator in the terminal, reconciled by walking it; a current comprehensive report per unit to SANS 1545-1:2016 ed 3.6 at the two-yearly cycle or on contractor change; the Appointed Inspector's appointment letter; and the certificate displayed at each unit current and matching that unit's ID. Records retained ten years. | evidence stub: 'LI certificates; register' duplicates MEC-019 through MEC-027 | keep only the register completeness and the displayed-certificate check — walk the terminal, count the units, reconcile against the register
KSIA-MEC-029 | Mechanical | People Movers | Condition | Visual: step/pallet gaps, comb plates, handrail cracks, landing plates secure, skirt brushes, emergency stops, signage. | Site Physical Verification | Asset | examine | The one People Movers check decided entirely on the machine. A broken comb tooth and a cracked handrail are seen and felt, and no certificate discloses them. | Physically inspect each escalator/travelator: check the gap between steps/pallets and skirt panels, confirm comb plates are intact with no missing teeth and mesh properly with the steps, check handrails for visible cracks or fraying, press/wobble landing plates to confirm they're secure, confirm skirt brushes are present along the step edges, locate the emergency stop buttons and check they're undamaged and accessible, and confirm safety signage is present and legible. | Step/pallet-to-skirt gaps within tolerance, no two adjacent comb teeth broken, handrails uncracked and un-frayed, landing plates secure, skirt brushes fitted, emergency stops present and unobstructed, signage legible. | evidence stub: 'Site inspection'
KSIA-MEC-030 | Mechanical | Passenger Boarding Bridges (PLBs) | Passenger Boarding Bridges (PLBs) | Safety systems Test records | Evidence + Site Physical Verification | Document | examine | Four safety systems, each with its own OEM test. The record must show all four were exercised — the easy ones alone is the common failure. | At the PLB, where a test can be observed, check that all four safety-system categories are actually exercised (not just the easiest to check), and confirm the test frequency matches what the OEM schedule specifies. | OEM functional test at the FALE four-monthly cycle covering auto-levelling, bumper/obstruction sensors, emergency stop and cabin interlock.
KSIA-MEC-031 | Mechanical | Passenger Boarding Bridges (PLBs) | Passenger Boarding Bridges (PLBs) | COC | Evidence + Site Physical Verification | Document | reconcile | As MEC-009, for the bridge's supply and control installation, matched to the gate number. | At the PLB, check the bridge/gate number against the CoC, and confirm no relocation or control-system upgrade has occurred since the CoC was issued. | Current CoC for the PLB's electrical supply/control installation, issued by a registered person. | requirement is one word, 'COC' — no scope, no interval, no issuing authority stated in the check itself
KSIA-MEC-032 | Mechanical | Passenger Boarding Bridges (PLBs) | Passenger Boarding Bridges (PLBs) | 2 yearly Structural Integrity inspections | Evidence + Site Physical Verification | Document | examine | Welds, bogies and undercarriage corrosion are assessed by a competent person with access the auditor does not have. The report's SCOPE is the check. | At the PLB, visually inspect the visible support structure and, if accessible, the wheel bogies/undercarriage for corrosion or visible weld damage; check whether the report covers the undercarriage or only the visible cabin structure. | Two-yearly report explicitly covering welds, support structure, wheel bogies/undercarriage and corrosion — not only the visible cabin structure. | conflicting intervals in the source: FALE's own cycle is 2-yearly in years 2 and 4, against a counter-benchmark of a three-monthly visual structural inspection
KSIA-MEC-033 | Mechanical | Passenger Boarding Bridges (PLBs) | Structural integrity | Structural assessment by an ECSA-registered Professional Engineer covering corrosion, welds, rotunda, tunnel and wheel bogie; remedial actions closed. | Evidence + Site Physical Verification + Question | Document | examine | A PrEng structural assessment is a professional opinion in a report. | 1. At each PLB, visually check the areas the report should cover — visible corrosion or paint failure, weld condition where visible, condition of the rotunda and tunnel structure, and the wheel bogie — and compare against what the report describes. 2. Where remedial work was recorded as closed out, check the relevant area on the PLB to confirm the repair is actually visible and complete. | A structural assessment report by an ECSA-registered Professional Engineer covering corrosion, welds, rotunda, tunnel and wheel bogie, with every remedial action closed. NOTE: ACSA's D080 029M requires no such report — treat a missing one as a gap in ACSA's manual to be raised, and demand instead the counter-benchmark D080 028M cl. 4.2.5 six-monthly/yearly structural inspection by a competent person. | evidence stub: 'PrEng structural assessment report' ACSA's own manual requires NO such report — the register's acsaEvidence field says '(none required by D080 029M)'. The check demands evidence ACSA does not oblige anyone to hold. duplicates MEC-032 | merge into MEC-032, and raise the missing PrEng requirement as a policy gap against ACSA rather than as a site non-compliance
KSIA-MEC-034 | Mechanical | Passenger Boarding Bridges (PLBs) | Operation & safety | Auto-leveller, safety shoe, canopy, drive/steer and emergency stop tested; operator authorisation register; PM completed per OEM. | Evidence + Site Physical Verification | Asset | examine | Auto-leveller, safety shoe, canopy and emergency stop are demonstrated on the bridge by an operator. That demonstration, not the PM sheet, is what settles it. | 1. At a PLB, ask the operator or a technician to demonstrate the auto-leveller adjusting, check the safety shoe is present and moves freely, inspect the canopy for damage or gaps, and locate the emergency stop button and check it's undamaged and accessible. 2. Ask the operator on duty to show their authorisation/ID and check their name appears on the register. | The auto-leveller demonstrated adjusting, the safety shoe present and moving freely, the canopy undamaged and without gaps, drive/steer working and the emergency stop located and functional — plus the four-monthly FALE task tables completed, faults carrying an IMC reference number, and an operator authorisation register naming everyone who drives the bridge. | evidence stub: 'PM records; operator register' overlaps MEC-030, which tests the same four systems from the record side | keep the demonstration here; the OEM test record is MEC-030; the operator authorisation register is a Document check of its own
KSIA-MEC-035 | Mechanical | Fuel System | Fuel System | A valid AIA developed MHI Risk Assessment | Evidence + Site Physical Verification | Document | reconcile | An MHIR reg 5 risk assessment by an Approved Inspection Authority, five-yearly. The walk checks the fuel farm has not outgrown what it covers. | Walk the fuel farm/tank hydrant configuration and compare it against what the risk assessment describes — flag if the site has since expanded (new tanks/hydrants) beyond what the assessment covers. | Current AIA MHI risk assessment within 5 years, proof of submission to the Chief Inspector, local and provincial government, and a tank/hydrant configuration matching what it assessed.
KSIA-MEC-036 | Mechanical | Fuel System | Fuel System | A 3 yearly valid On-site Emergency Plan | Evidence + Site Physical Verification + Question | Document | reconcile | The plan is a document; whether it was drilled is a record of an event. The walk checks the plan still describes the site it is for. | 1. Compare the emergency plan's site layout/emergency contact list against the current physical site — flag any mismatch (renamed buildings, changed access routes, outdated contacts). 2. Ask to see the drill records/photos/attendance sheets from the most recent annual drill and confirm they correspond to an actual exercise, not merely a paper sign-off. | 1. Current on-site emergency plan, reviewed/updated in consultation with the local authority within the last 3 years (MHIR reg 6(1)(c)). 2. Records of the annual practical drill of the plan (MHIR reg 6(1)(g)). | requirement says 3-yearly but ACSA requires the plan TESTED at least every 12 months and SUBMITTED to NERSA annually — three different clocks in one check | split in two — the plan's currency and consultation with the local authority (Document), and the annual practical drill (Practice)
KSIA-MEC-037 | Mechanical | Fuel System | Fuel System | A 3 yearly and AIA witnessed Piping Pressure test records | Evidence + Site Physical Verification + Question | Document | examine | A witnessed pressure test certificate. The AIA's stamp is the point — a contractor's own sign-off is not the same document. | Check the certificate's AIA signature/stamp is present (not just a contractor's own sign-off), and confirm the tested sections cover the full piping network (tank farm and hydrant lines), not just part of it. | AIA-witnessed certificate within ONE year for FALE, stating test pressure and result, covering the tank farm AND the hydrant lines. | DIRECT CONFLICT: the check says 3-yearly, ACSA D060 021M cl. 4.17.5 says the hydrant line pressure test at FALE (King Shaka) is YEARLY. Auditing FALE against 3 years would pass an installation that is two years overdue.
KSIA-MEC-038 | Mechanical | Fuel System | Fuel System | ASME B31.3 Piping Designs | Evidence + Site Physical Verification + Question | Document | reconcile | A design package and its certification. The walk spot-checks material spec plates against it and finds the older sections nobody has documentation for. | 1. Where design documentation exists, spot-check a visible section of piping (markings, material spec plates) against the design package; flag any older piping section for which no design documentation is available on site. | Piping design package certified to the code ACSA actually adopts, plus the Petroleum Pipeline Act construction licence, with documentation covering every section including the oldest. | CONFLICTING CODE: the check names ASME B31.3; ACSA D060 021M cl. 4.15.1 names API/IP 1540 plus JIG. No wall-thickness or design criterion is stated for either.
KSIA-MEC-039 | Mechanical | Fuel System | Fuel System | Quarterly Calibration records of potable gas meters | Evidence + Site Physical Verification + Question | Document | reconcile | A calibration certificate against a serial number. The walk exists to catch a bump test recorded as a calibration, which is the routine substitution here. | Check the meter's serial number/tag on site matches the certificate on file; ask whether the last "calibration" was a full calibration or only a bump test, since the two are often conflated. | Full calibration certificate — not a bump test — from a competent provider, referencing the meter serial number found on the instrument. | 'potable gas meters' — almost certainly PORTABLE gas meters; the register carries the typo ACSA names four calibration items (crawl beams, gauges, hydrocarbon detectors, tightness control system) and NO quarterly interval
KSIA-MEC-040 | Mechanical | Fuel System | Fuel System | ESB Test records | Evidence + Site Physical Verification + Question | Document | reconcile | The record must show fuel flow actually stopped, not that a button was pressed. The walk confirms staff know what the button isolates. | Physically locate the ESB device/button referenced and confirm site staff can identify what system it isolates; where a test can be observed, confirm the record shows the actual valve/pump isolation occurred, not just that the button was pressed. | Functional test showing the valve or pump actually isolated, plus the approved Safe Work Procedure for emergency fuel hydrant shut-off signed by the GMR 2(1) and 2(7) appointees. | ACSA does not define 'ESB'; the manual's term is ESD, maintained six-monthly at FALE. The check and the manual may not be describing the same device.
KSIA-MEC-041 | Mechanical | Fuel System | Fuel System | Updated As-Built Drawings of the system | Evidence + Site Physical Verification | Document | reconcile | An as-built is compliant only against the tank farm it claims to describe. That comparison is the whole check. | Walk the tank farm/piping/hydrant layout and compare it against the as-built drawing on hand — flag any physical feature (tank, valve, hydrant) not shown on the drawing, or vice versa; check the drawing carries version control. | Version-controlled as-built set in PDF and native format, named by project/drawing/revision, minimum A3, with no tank, valve or hydrant on site missing from it and none on it missing from site.
KSIA-MEC-042 | Mechanical | Fuel System | Fuel System | Cathodic Protection records | Evidence + Site Physical Verification | Document | reconcile | Pipe-to-soil potential is a millivolt reading against a criterion. Only the log has it; the walk confirms the rectifier is actually being read. | At the rectifier station(s), check the current reading/log against the required interval; confirm records identify which specific pipe section or tank each reading relates to, and check whether any out-of-range reading has a linked corrective action. | Readings at the site's stated interval, each identifying the pipe section or tank it relates to, against -850 mV CSE, with a linked work order for any out-of-range reading. | the -850 mV CSE criterion is in the check's evidence but nowhere in ACSA's threshold — ACSA states intervals only
KSIA-MEC-043 | Mechanical | Fuel System | Fuel System | Buried piping external coating spot inspection records | Evidence + Site Physical Verification + Question | Document | none | Buried coating can only be seen during an excavation or inferred from a close-interval survey. On a normal audit there is nothing to look at. | — nothing to inspect on site | Coating-integrity records from any excavation in the period, or a close-interval survey — and where neither exists, that stated as the reason rather than left blank. | no coating inspection interval and no holiday-test criterion in ACSA the check may be unanswerable in an audit period with no excavation — it needs an explicit 'not applicable this period' outcome rather than a fail
KSIA-MEC-044 | Mechanical | Fuel System | Fuel System | Hydrant pit box and valve chamber | Evidence + Site Physical Verification | Asset | examine | You open the pit and look in. Water ingress, a failed seal and an unrated fitting are all read on the spot. | Open (or observe) a sample of hydrant pits and valve chambers on the apron; check for standing water or fuel ingress, confirm drainage/sealing looks intact, and check any electrical equipment inside is rated for its hazardous-area zone. | Pit box and chamber intact, draining, sealed, with any electrical equipment inside rated for its hazardous-area zone. | duplicates MEC-046 (lids) and MEC-054 (couplers, seals, lids, water)
KSIA-MEC-045 | Mechanical | Fuel System | Fuel System | Hydrant pit valve integrity test records | Evidence + Site Physical Verification + Question | Document | reconcile | Leak-tightness is a measured rate. The walk counts pit valves against the records, because partial coverage is the usual state. | Cross-check the apron's hydrant pit valve array against the test records to confirm every pit valve has been tested, not just some; check whether the maintenance manual referenced actually exists on site and states a required frequency. | A test record for EVERY pit valve, and the maintenance manual it references actually existing on site with a stated frequency. | ACSA notes 'leak rate is to be noted but NO numeric limit' — the check has no pass mark to test against
KSIA-MEC-046 | Mechanical | Fuel System | Fuel System | Pit lid integrity inspection (Anodising, seals and functionality) | Evidence + Site Physical Verification | Asset | examine | Corrosion, a perished seal and a lid that will not close are seen on the apron, and each is a trip or FOD hazard in its own right. | Walk the apron and visually check hydrant pit lids for corrosion, damaged seals or difficulty opening/closing; flag any lid left damaged/corroded as an in-service trip or FOD hazard, and cross-check coverage against the full field of lids. | Pit lid inspection records (corrosion/anodising condition, seal condition, opening/closing functionality) for each hydrant pit lid. Any defective lids and remedial action taken. | no acsaThreshold for anodising, seal condition or lid functionality — daily inspection is required but no criterion is given duplicates MEC-044 and MEC-054 | one hydrant pit condition check covering box, chamber, lid, seals and couplers
KSIA-MEC-047 | Mechanical | Fuel System | Fuel System | Hydrant pit valve dynamic test (valve closing test) | Evidence + Site Physical Verification + Question | Document | examine | The distinction between a dynamic and a static test is only visible in how the record describes the conditions. Nothing on the apron tells you which was done. | Where a live or recent dynamic test can be reviewed, confirm the record actually describes an under-flow (dynamic) test, not a static (no-flow) test recorded as if it were dynamic; check whether any valve failed to seal fully but was still recorded as a pass. | A record describing an under-flow closing test with the flow condition stated, and a linked corrective action for any valve that failed to seal. | no acsaThreshold at all for a dynamic closing test
KSIA-MEC-048 | Mechanical | Fuel System | Fuel System | Annual Meter Proving records | Evidence + Site Physical Verification | Document | reconcile | Meter proving is a metrological certificate against a serial number, and the walk exists to find the meter that has none. | At the meter installation, check the meter's identification/serial number against the certificate; confirm every meter on site (not just some) has a current proving certificate, and check that any meter shown outside tolerance had a correction factor applied. | Current proving certificate for EVERY dispensing or custody-transfer meter, with the NRCS verification where applicable, and an out-of-tolerance result followed by adjustment and re-prove. | ACSA's calibration list names Gauges but not custody-transfer meter proving; no annual proving interval is stated
KSIA-MEC-049 | Mechanical | Fuel System | Fuel System | Internal Tank Integrity Inspection records | Evidence + Site Physical Verification | Document | examine | An internal inspection happens inside an emptied tank. The report and its calculated next-due date are the only access an auditor has. | Where the tank is accessible, check the external shell/foundation for visible corrosion or leakage staining consistent (or not) with the inspection report's findings; confirm the report states a remaining-life or next-due date calculated from an actual corrosion-rate assessment, not an assumed interval. | Inspection report with bottom-plate thickness readings and a calculated remaining life or next-due date, and no external shell staining that contradicts it. | API 653 is named in the check's evidence but not by ACSA — ACSA requires five-yearly CLEANING, which is a different operation from an integrity inspection
KSIA-MEC-050 | Mechanical | Fuel System | Fuel System | Hazardous area classification map for bulk storage sites | Evidence + Site Physical Verification | Document | reconcile | A zone map is a drawing. It is compliant when it matches the plant, and the way to test that is to stand in a zone and read an equipment rating. | Walk the bulk storage site and compare the zone map against the physical tank farm/pipework layout, especially after any expansion; spot-check a piece of electrical equipment in the field against the Ex-rating the map implies for that zone. | Current zone classification drawing reflecting the plant as it now stands, with field equipment carrying at least the Ex rating its zone requires. | no acsaThreshold — SANS 10108 is named only in the check's own evidence field
KSIA-MEC-051 | Mechanical | Fuel System | Fuel System | Integrity inspection of electrical equipment in hazardous areas | Evidence + Site Physical Verification | Document | reconcile | SANS 10086 inspection grades are recorded, not observed. The walk samples glands and enclosures and checks the register covers what is installed. | In a hazardous-area zone, check a sample of Ex-rated equipment's glands and enclosures for visible damage or looseness; confirm the equipment inspected matches what's on the hazardous-area equipment register, and check whether the correct inspection grade (visual/close/detailed) was performed when a detailed inspection was due. | Periodic inspection records (SANS 10086 visual/close/detailed categories) for Ex-rated electrical equipment in hazardous-area zones. Inspection grade, date, and findings. | overlaps MEC-053, which reads the same nameplates for the same zones | keep the periodic inspection regime here; the Ex-certification of machinery is MEC-053
KSIA-MEC-052 | Mechanical | Fuel System | Fuel System | DB earth leakage, Wiring diagrams, COC | Evidence + Site Physical Verification + Question | Document | reconcile | Three separate checks — earth leakage, wiring diagram, CoC — bundled into one row for the fuel system. | 1. At the DB, check whether nearby electrical equipment is correctly Ex-rated for the zone it's in, and check the earth-leakage test record shows a measured trip current/time, not just a test-button check. 2. Compare the wiring diagram against the DB's actual internal layout, checking specifically for hazardous-area-related additions not shown on the diagram. 3. Check the CoC's asset reference against the DB in the field. | 1. Earth-leakage trip test record for the fuel system's DB. 2. As-built wiring diagram for the fuel system's DB. 3. Current CoC for the fuel system's DB. | three checks in one requirement, each already asked separately elsewhere duplicates MEC-012, MEC-010 and MEC-009 respectively | split three ways, or scope the single earth-leakage, diagram and CoC checks by asset system
KSIA-MEC-053 | Mechanical | Fuel System | Fuel System | Electrical machinery in hazardous locations to meet requirements of Incorporated standard such as SANS10089-2 | Evidence + Site Physical Verification | Asset | reconcile | An Ex mark is stamped on a nameplate you can read with a torch. Under-rated equipment in a Zone 1 is found by looking, not by reading a file. | In the hazardous-area zone, physically check the nameplate of installed electrical machinery for a valid Ex-certification mark, and confirm the equipment's rating matches (or exceeds) the zone it's actually located in — a lower-rated unit in a higher-risk zone is a fail. Check whether a register cross-referencing equipment to its zone exists. | Every machine in a hazardous zone carrying a valid Ex mark rated at or above its zone, cross-checked against SANS 10089-2 and the zone map.
KSIA-MEC-054 | Mechanical | Fuel System | Hydrant pits | Hydrant pit couplers, seals and pit lids intact; pits free of water/fuel; pit valve and lid inspection register maintained. | Evidence + Site Physical Verification + Question | Asset | examine | Couplers, seals, lids and standing water are all read by opening a pit. | 1. Open and physically inspect a sample of hydrant pits — check the coupler for damage, seals for cracking/perishing, and the lid for a secure, intact fit. 2. When a pit is opened, check by eye/smell whether there is standing water or any fuel present in the pit. 3. Cross-check the register entries against the physical pits inspected — confirm dates and findings in the register match what you observe on site. | Couplers undamaged, seals not cracked or perished, lids seating securely, no standing water or fuel in the pit by eye or smell, the weekly FALE fuel-on-water-table test done, daily inspection and cleaning records, and a pit valve and lid register covering every pit on the apron rather than a sample. | evidence stub: 'Pit inspection register; site walk' duplicates MEC-044 and MEC-046 | merge MEC-044, 046 and 054 into one hydrant pit condition check
KSIA-MEC-055 | Mechanical | Fuel System | Integrity & ESD | Hydrant line pressure/tightness test records; emergency shut-down (ESD) push-buttons tested; bonding at fuelling positions. | Evidence + Site Physical Verification | Document | examine | Pressure, tightness and ESD tests are all records; bonding continuity is a measured resistance. | 1. Visually check hydrant line access points/valve pits for any signs of fuel staining or leakage. 2. Locate ESD push-buttons at the fuelling positions/hydrant pits and check they are unobstructed, clearly marked and undamaged; ask for a safe demonstration/test if operationally possible. 3. At a fuelling position, locate the bonding cable/clip and check it is present, undamaged and not corroded. | The FALE hydrant line statutory pressure test within ONE year (not three), tightness control system maintained monthly with the leak rate noted, ESD maintained six-monthly with the push-buttons found unobstructed, clearly marked and undamaged at every fuelling position, and bonding continuity at fuelling positions measured — plus the approved Safe Work Procedure for emergency hydrant shut-off. | evidence stub: 'Test records' duplicates MEC-037 (pressure test), MEC-040 (ESD) and MEC-045 (tightness) bonding at fuelling positions appears nowhere else and has no ACSA threshold — it is the only new content in the row | delete the duplicated halves; keep bonding at fuelling positions as its own check
KSIA-MEC-056 | Mechanical | Fuel System | Fuel farm tanks | Tank in-service/out-of-service inspections, bund integrity & drainage, filter/water separator maintenance, product quality records. | Evidence + Site Physical Verification | Asset | examine | A bund wall crack, a blocked bund drain and a corroded tank shell are all seen. The product-quality records bundled in are not. | 1. At each tank, check the external inspection tag/plate for the last inspection date, and look for visible corrosion, coating failure or leaks on the tank shell and roof. 2. Physically inspect the bund wall for cracks or damage, confirm the bund is empty and dry, and that the drain valve is normally closed and not leaking. 3. Locate the filters/water separators and check service tags/labels for the last change date; check that a functioning water-drain point is in routine use. | External inspection tag on each tank current, shell and roof free of corrosion, coating failure and leaks; bund wall uncracked, dry and drain valve closed; five-yearly tank cleaning and ten-yearly flood survey records; weekly fuel filter and separator pit maintenance; a current Fuel Depot Licence; and product quality records for each grade. | evidence stub: 'Inspection certificates' overlaps MEC-049 for tank integrity four unrelated things in one row: tank inspection, bund integrity, filter/separator maintenance, product quality | split the bund and filter condition (Asset) from tank integrity (MEC-049) and product quality records (Document)
KSIA-MEC-057 | Mechanical | BHS | BHS | Conveyor interlocks, siren and trip test records | Evidence + Site Physical Verification | Asset | examine | You trip an interlock and the conveyor stops, or it does not. A defeated interlock is the finding and it is only visible at the machine. | 1. At a conveyor, trip (or observe a test of) a guarding interlock and confirm the conveyor physically stops; check for any interlock that appears bypassed or defeated for operational convenience. 2. Observe or review a siren test and confirm the siren is audible over ambient terminal noise before the conveyor begins moving. | Interlock trip observed stopping the belt, siren sounding before start-up on the monthly cycle, and no interlock bridged, taped or bypassed for throughput.
KSIA-MEC-058 | Mechanical | BHS | BHS | Conveyor Nip points Inspections | Evidence + Site Physical Verification | Asset | examine | A missing nip-point guard is seen from the walkway. No record substitutes for that. | Walk the conveyor lines and visually check nip points for guards fitted and intact; check for any guard propped open or missing after maintenance access, and check whether an interlock switch on a guard appears defeated/bridged out. | Every identified nip point guarded, guards intact and reinstated after maintenance, and no interlock switch on a guard bridged out. | overlaps MEC-057, MEC-062 and MEC-065 — four checks walking the same conveyor guarding
KSIA-MEC-059 | Mechanical | BHS | BHS | Carousel siren test records | Evidence + Site Physical Verification | Asset | examine | Whether a siren is audible over terminal noise, and whether it precedes motion by a real margin, has to be heard. | Observe (or review evidence of) a carousel start and confirm the siren is audible over terminal noise and sounds with an adequate margin before the carousel actually moves, not merely that it sounds at some point. | Siren heard above ambient terminal noise, sounding with a stated margin before the carousel moves — and a documented required duration to measure that margin against. | no acsaThreshold — no siren duration or margin before motion is stated anywhere duplicates MEC-063 for the sorter
KSIA-MEC-060 | Mechanical | BHS | BHS | Localised Conveyor and carousel E-stop test records | Evidence + Site Physical Verification | Asset | examine | An E-stop is pressed and the line halts with no auto-restart. Damage and obstruction are seen at the same time. | Walk the conveyor/carousel line, physically test (or observe a test of) a sample of E-stop buttons/pull-cords, confirm immediate halt with no auto-restart, and check for any E-stop that is physically damaged or obstructed. | Sample of E-stops physically tested, immediate halt with deliberate manual reset, none damaged or obstructed.
KSIA-MEC-061 | Mechanical | BHS | BHS | Carousel roller shutter doors , fire detection and carousel interlock test records | Evidence + Site Physical Verification | Document | examine | What matters is whether the shutter was triggered BY the fire alarm or closed by hand and written up as if triggered. Only the record and the cause-and-effect matrix show that. | 1. Where a test can be observed, confirm the shutter is actually triggered via the fire alarm system, not manually operated and recorded as if alarm-triggered; check a cause-and-effect matrix exists on site to confirm the correct response is defined. 2. Observe or review evidence of the shutter-to-drive interlock test, checking specifically that the closing sequence is verified against a moving carousel, not just a stationary one. | Test records for both directions — closure on fire alarm and the carousel interlock — cross-referenced to a cause-and-effect matrix held on site.
KSIA-MEC-062 | Mechanical | BHS | BHS | Sorter/Conveyor Interlock test records | Evidence + Site Physical Verification | Asset | examine | Same physical test as MEC-057, across the sortation system. | Walk the sortation system and check whether interlock zones are being bypassed to maintain throughput during peak periods; confirm test records cover all interlock zones across the system, not a partial sample. | Interlock test records across the sortation system's conveyors, showing each interlock zone tested for guarding/safety-interlock integrity. | duplicates MEC-057 and MEC-058 | merge into MEC-057, scoped to cover every interlock zone rather than a sample
KSIA-MEC-063 | Mechanical | BHS | BHS | Sorter siren test records | Evidence + Site Physical Verification | Asset | examine | Same audible test as MEC-059, on the sorter. | Observe (or review evidence of) a sorter start and confirm the siren is audible over ambient noise and precedes motion by an adequate margin. | Sorter warning siren functional test record confirming the siren sounds for the required period before the sorter begins moving. | duplicates MEC-059 | one siren check covering carousel and sorter
KSIA-MEC-064 | Mechanical | BHS | BHS | DB Earth leakage test records, Inspection records of Electrical/Control wiring diagrams | Evidence + Site Physical Verification | Document | reconcile | Two checks in one, both already asked elsewhere, scoped to the BHS control DBs. | 1. At the BHS control DB, check for evidence of a measured trip test and confirm the panel hasn't been reconfigured since the last test without a re-test. 2. At the BHS control panels, spot-check the wiring against the diagram given these panels are frequently reconfigured; check the CoC date against any recent control panel upgrade. | 1. Earth-leakage trip test record for the BHS control system's DB(s). 2. Current CoC and as-built wiring diagrams for the BHS control system's DB(s). | duplicates MEC-012 (earth leakage) and MEC-010 (wiring diagrams and CoC)
KSIA-MEC-065 | Mechanical | BHS | Safety & maintenance | Guarding, emergency stops, lock-out procedure, conveyor PM completion rate, spares for critical drives. | Evidence + Site Physical Verification | Asset | examine | Guards and E-stops are the physical half and already covered above. Lock-out is a procedure and spares holding is a stores record — neither is a condition. | 1. Walk the BHS and visually check guards are fitted over all moving parts, drive units and pinch points, and that none are missing, propped open or bypassed. 2. Locate E-stop buttons/cords along the conveyor route and check they're accessible, undamaged and clearly marked; ask for a safe demonstration/test if operationally possible. 3. Ask a technician to describe or demonstrate the lock-out steps they'd follow before clearing a jam or working on a conveyor. 5. Ask to see the spares store/shelf for critical drive spares and check stock is physically present, not just listed on paper. | Guards fitted over every moving part, drive unit and pinch point with none missing, propped or bypassed; E-stops present, reachable and unobstructed along the route; a documented lock-out/tag-out procedure with records of its use; PM scheduled at least thirty days ahead with deviation admin closed within one workday; and critical drive spares held at the minimum quantity (annual usage / 12 months) on the KARDEX card. | evidence stub: 'CMMS PM reports' duplicates MEC-057, MEC-058 and MEC-060 three different check types in one row | split three ways — guarding and E-stops (already MEC-057/058/060), lock-out/tag-out procedure and its records (Practice), critical drive spares holding (Document)
KSIA-MEC-066 | Mechanical | Fire Protection - Fire Extinguishers | Fire Protection - Fire Extinguishers | Extinguisher pressure test records | Evidence + Site Physical Verification | Asset | reconcile | The hydrostatic test date is stamped on the cylinder. You read it off the extinguisher standing in front of you. | Physically check the pressure-test date stamp on each extinguisher's tag/cylinder, confirming it's legible and current; specifically check CO2 cylinders are checked against their own (not the water/foam) interval table. | Legible test stamp on each cylinder within the SANS 1475-1 interval for its TYPE — CO2 read against the CO2 table, not the water/foam one.
KSIA-MEC-067 | Mechanical | Fire Protection - Fire Extinguishers | Fire Protection - Fire Extinguishers | Extinguisher Inspection records | Evidence + Site Physical Verification | Asset | examine | In its logged location, gauge in the green, pin and seal intact, undamaged — every element is read on the unit. | Physically inspect the extinguisher: confirm it's in its logged location, accessible, pressure gauge needle in the green zone, seal/pin intact, and no visible damage; check the monthly log for gaps. | Extinguisher present where the register says, accessible, needle in the green, seal and pin intact, no damage — and the inspection log without gaps. | ACSA requires inspection QUARTERLY; the check's evidence asks for a MONTHLY visual log — two different intervals in one check
KSIA-MEC-068 | Mechanical | Fire Protection - Fire Extinguishers | Servicing | Annual service by SANS 1475-accredited provider; hydrostatic test dates; monthly inspection tags; correct type/location. | Evidence + Site Physical Verification | Asset | reconcile | A roll-up of MEC-066 and MEC-067 with one addition: whether the type and location match the fire hazard class of the area. | 1. Check the service tag physically attached to a sample of extinguishers for the last annual service date and provider details. 2. Check the hydrostatic test date stamped on the cylinder body/neck against the required retest interval. 3. Check the monthly inspection tag on each extinguisher for signed entries with no gaps, and check the pressure gauge needle is in the green/operating zone. 4. Confirm the extinguisher type matches what's required for the area (e.g. CO2 near electrical panels, not water), and that it is mounted at the correct height, unobstructed and visible, with signage. | Service tag on each extinguisher showing an annual service within twelve months by a SANS 1475-accredited provider with the provider named; the hydrostatic date stamped on the cylinder within the retest interval FOR ITS TYPE; inspection tags with no gap in the quarterly cycle; and the type and size at each location matching the area's SANS 10400-T fire hazard class. | evidence stub: 'Service tags; register' duplicates MEC-066 and MEC-067 | keep only 'correct type and location for the area's fire hazard class', which nothing else asks, and reconcile it against MEC-069
KSIA-MEC-069 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Record of Fire Hazard Classes for each occupancy | Evidence + Site Physical Verification | Document | reconcile | A SANS 10400-T classification per occupancy. It fails when an area's actual use has moved on from the class it carries — which is a walk, not a read. | Walk each occupancy/area and check its current use against the classification record — flag any area where the actual use (e.g. office converted to storage) no longer matches the classified fire load, and check the record covers the whole facility, not just some areas. | A classification record covering every occupancy, and each area's current use still matching its assigned fire load — an office turned into a store is the failure.
KSIA-MEC-070 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Valve station Block Plans | Evidence + Site Physical Verification | Document | reconcile | A block plan is only useful at the valve station in an emergency. Held centrally, it fails the purpose even if it exists. | At each valve station, check whether a physical copy of the block plan is actually available on site (not only held centrally), and check the valve numbering on the plan matches the physical tags in the field. | A physical copy of the SANS 10287 block plan at each valve station, with valve numbering matching the tags in the field.
KSIA-MEC-071 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Hose reel Maintenance/test records | Evidence + Site Physical Verification | Document | examine | A flow and pressure figure is the test. A visual 'hose OK' recorded as a test is the failure, and only the record discloses it. | At the hose reel, physically run out the hose (or review the last test) and check the isolating valve isn't seized; confirm the record shows an actual flow/pressure check was performed, not just a visual "hose OK". | SANS 10105-2 record showing an actual flow/pressure check against design flow, hose and nozzle condition, isolating valve free — plus SANS 1475-2 reconditioning certificates for any reel sent away.
KSIA-MEC-072 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Annual Fire hydrants test records | Evidence + Site Physical Verification | Document | reconcile | Measured L/s and residual bar, compared against the fire-engineering design values. The comparison is the check — a recorded number with nothing to compare it to proves nothing. | At a sample of hydrants, check the test date is within 12 months, confirm the hydrant isn't seized or leaking, and check the record's measured flow/pressure was actually compared to the design report rather than just recorded. | Annual test per hydrant with measured flow and residual pressure explicitly compared to the design report, and the hydrant free and not leaking at the gland.
KSIA-MEC-073 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Quarterly Sprinkler head Inspection records | Evidence + Site Physical Verification + Question | Asset | examine | A painted-over head, stock stacked into the spray pattern and a corroded rosette are all seen from below. | Walk a sample of sprinkler-protected areas and visually check heads for paint-over, obstruction (stock stacked too close), corrosion or physical damage; check the inspection record is itemised by zone/head, not a generic sitewide sign-off. | Heads unpainted, unobstructed, uncorroded, correctly oriented — and an inspection record itemised by zone rather than a sitewide sign-off.
KSIA-MEC-074 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Weekly Valve station Water flow alarm tests (30 Seconds) | Evidence + Site Physical Verification | Document | examine | Thirty seconds is a measured elapsed time on a log. The walk can watch one test, but the weekly series is the compliance. | Where a test can be observed, open the inspector's test valve and time the alarm activation against the 30-second target; confirm the alarm signal reaches the monitored fire control room/BMS, not just a local sounder. | Weekly log per valve station recording the elapsed time to alarm against the 30-second target, and the signal reaching the monitored fire control room — not just a local sounder.
KSIA-MEC-075 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | 3 yearly Deluge/Control Valve service records | Evidence + Site Physical Verification | Document | reconcile | A service record from an ASIB-registered or insurer-approved provider, identifying which valve of which zone. | At the deluge/control valve station, check the service record's date against the physical valve and confirm it identifies the specific valve(s) serviced, given the site may have multiple deluge zones. | Service record at the interval ACSA actually requires, naming the specific valves serviced across every deluge zone. | CONFLICT: the check says 3-yearly, ACSA D080 002M cl. 4.7.8 says deluge/control valve service records YEARLY
KSIA-MEC-076 | Mechanical | Fire Protection - Hose reels and fire hydrants | Fire Protection - Hose reels and fire hydrants | Yearly Independent ASIB Inspection | Evidence + Site Physical Verification | Document | reconcile | An ASIB Certificate of Inspection. Its coverage is the question — a multi-building network partly certificated reads as compliant until you compare. | Check the certificate's date and coverage against the physical sprinkler network — confirm it covers the whole multi-building network, not just part of it, and check whether any noted defect has since been fixed. | Certificate within 12 months covering the whole sprinkler network, with noted defects closed. | ACSA qualifies this '(if applicable)' and never says when it applies — the check has no applicability rule
KSIA-MEC-077 | Mechanical | Fire Protection - Hose reels and fire hydrants | Testing | Annual flow/pressure tests; hydrant valve operation; hose reel condition; signage & access unobstructed. | Evidence + Site Physical Verification | Asset | examine | Operating a hydrant valve, unreeling a hose and checking access is unobstructed are all done on the equipment. | 1. Check the test tag/label on the hydrant for the last test date. 2. At a sample hydrant, operate the valve (if permitted/safe) to check it turns smoothly without excessive force and doesn't leak at the gland. 3. Unreel a sample hose reel partway to check the hose is not cracked, perished or damaged, that it winds back freely, and the nozzle is present and undamaged. 4. Walk to each hydrant/hose reel and confirm signage is present, visible and not obscured, and that nothing is blocking access to it. | Test tag on each hydrant within date, the valve turning smoothly without excessive force and not leaking at the gland, hose reels unreeled with the isolating valve free and the hose sound, signage present and access unobstructed — plus valve station flow and pressure tests at the MONTHLY interval ACSA requires, not annually. | evidence stub: 'Test records' duplicates MEC-071 and MEC-072 INTERVAL CONFLICT: the check says annual flow/pressure tests; ACSA requires valve station flow and pressure tests MONTHLY | keep signage and unobstructed access, which nothing else covers; the tests are MEC-071/072/074
KSIA-MEC-078 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Quaterly 6h Diesel Full load Engine test run | Evidence + Site Physical Verification | Document | examine | Six hours at load is a duration and a load figure in a log. 'Ran OK' is the failure and only the log shows it. | Where a test can be observed or recent evidence reviewed, confirm the log records actual load/pressure achieved (not just "ran OK"), and check the duration matches 6 hours, not a shortened run. | Quarterly log stating the actual load or pressure achieved and a full six-hour duration, with any alarm or fault recorded.
KSIA-MEC-079 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Electric-to-diesel pump automatic switch over test | Evidence + Site Physical Verification | Document | examine | The record must show a simulated failure, not a manual switch. Only its description distinguishes them. | Where possible, observe or review evidence of a genuine simulated-failure changeover test (not just a manually forced switch), and check the record states the changeover time against the design starting time. | Monthly record of a genuine simulated pressure-loss or power-failure changeover, stating the changeover time against the design starting time.
KSIA-MEC-080 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Monthly Battery test records | Evidence + Site Physical Verification | Document | examine | State of charge and starting capability are measured. The walk's contribution is checking BOTH batteries of a dual set were tested. | At the fire pump station, check both batteries of a dual-battery set are actually tested (not just one), and check whether any marginal test result was followed by replacement. | Monthly log per battery — both of a dual set — with a result, and a replacement following any marginal result.
KSIA-MEC-081 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Pressure gauge and water level records | Evidence + Site Physical Verification | Document | reconcile | The gauge on the wall gives today's reading; the log gives the series. The check is the two agreeing, against the design values. | At the fire pump station, read the current pressure gauge and tank/reservoir level and compare against the log and the design values; check the pressure gauge itself is calibrated/verified accurate, and check whether a repeatedly low water level has been actioned. | Weekly pressure and level log against fire-engineering design values, the gauge itself verified accurate, and a repeatedly low reading investigated rather than logged.
KSIA-MEC-082 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Battery charger test records | Evidence + Site Physical Verification | Document | examine | A charger test and a battery test are routinely conflated into one entry. Only the record shows whether the charger was actually exercised. | At the fire pump station, check the charger's indicator/readout if available, and confirm the test record clearly distinguishes the charger test from the battery test rather than conflating the two. | A monthly record that names the charger test distinctly from the battery test and confirms correct float-charging. | overlaps MEC-080 in practice — the two are commonly recorded as one test
KSIA-MEC-083 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Suction and discharge Valve test records | Evidence + Site Physical Verification | Asset | examine | Locked and sealed open is a physical state of a valve. You look at the padlock. | At the fire pump station, physically check the suction and discharge valves are in the locked/sealed open position (not left free to be closed accidentally), and where possible confirm they aren't seized. | Suction and discharge valves found locked or sealed in the open position, free to operate and not seized, with the monthly exercising record.
KSIA-MEC-084 | Mechanical | Fire Protection - Fire Water pump station | Fire Protection - Fire Water pump station | Diesel level checks | Evidence + Site Physical Verification + Question | Document | reconcile | Level against the minimum runtime in the design basis. The walk reads the tank and checks fuel quality was actually looked at, not assumed. | At the fire pump's day tank, check the current fuel level against the log, and check whether fuel quality (water contamination, diesel bug) was actually checked alongside the level, not just assumed. | Weekly level log with the reserve meeting the design runtime, and evidence that water contamination and diesel bug were checked, not just the level.
KSIA-MEC-085 | Mechanical | Fire Protection - Fire Water pump station | Testing | Weekly churn test, annual flow test, diesel pump batteries/fuel, jockey pump & pressure logs; tank levels. | Evidence + Site Physical Verification | Document | examine | A roll-up of the seven pump-station checks above. | 1. At the pump house, check the churn test log is posted/available and up to date, and if possible ask for the pump to be started so you can observe it running. 2. Check the last flow-test date/tag on the pump and its general condition. 3. Physically check the diesel pump's battery terminals (clean, connected) and fuel gauge/tank level. 4. Check the pressure gauges on the jockey pump/system for a current, sensible reading (not zero, not obviously abnormal). 5. Physically check the fire water tank level gauge/sight glass against the recorded minimum level requirement. | Weekly pressure gauge, water level and diesel level logs; monthly battery, charger, valve and electric-to-diesel switch-over tests; the quarterly six-hour diesel full-load run per SANS 10287 cl. 10.1 with the load achieved recorded; and tank levels against design. NOTE: 'churn test' and 'jockey pump' appear nowhere in ACSA's manual — confirm they are required before auditing against them. | evidence stub: 'Test logs' duplicates MEC-078 through MEC-084 introduces two terms — 'churn test' and 'jockey pump' — that appear nowhere else in the register and have no ACSA threshold | delete the duplicated halves; keep the churn test and the jockey pump as their own checks IF ACSA's manual actually requires them, which needs confirming first
KSIA-MEC-086 | Mechanical | Sewer, Potable & Stormwater Pumps | Sewer, Potable & Stormwater Pumps | Sewer sump gas monitor calibration records | Evidence + Site Physical Verification | Document | reconcile | A calibration certificate against a serial number, plus daily bump tests. The walk proves the certificate belongs to the monitor actually carried into the sump. | Physically check the gas monitor's serial number against the calibration certificate to confirm it's the actual unit used in the field (not a spare); check the monitor is configured to detect H2S, LEL and O2 as appropriate for a sewer environment. | Calibration certificate matching the serial number of the unit in field use, daily bump-test records before each entry, and the monitor configured for H2S, LEL and O2. | no acsaThreshold — no gas monitor calibration interval is stated
KSIA-MEC-087 | Mechanical | Sewer, Potable & Stormwater Pumps | Sewer, Potable & Stormwater Pumps | Earth leakage test | Evidence + Site Physical Verification | Document | examine | A measured trip current and time in a test record. | At the pump control panel, check for evidence the panel hasn't been modified since the last earth-leakage test without a re-test. | Earth-leakage trip test record for the pump motor/control panel circuits. | fifth of six near-identical earth-leakage rows: MEC-012, 052, 064, 087, 092, 102 | one earth-leakage check scoped by asset system
KSIA-MEC-088 | Mechanical | Sewer, Potable & Stormwater Pumps | Sewer, Potable & Stormwater Pumps | Records of inspections for Guarding of moving parts | Evidence + Site Physical Verification | Asset | examine | A guard is fitted or it is lying beside the pump. That is seen. | At each pump, visually check couplings/shafts for fitted, undamaged guards; check for any guard removed for maintenance access and not reinstated, or present but loose/damaged. | Every coupling and shaft guarded, guards undamaged and reinstated after maintenance access, grid covers in place with their limit switches working.
KSIA-MEC-089 | Mechanical | Sewer, Potable & Stormwater Pumps | Sewer, Potable & Stormwater Pumps | Panel wiring diagram and COC validity check | Evidence + Site Physical Verification | Document | reconcile | Two checks in one — diagram and CoC — for the pump control panel. | 1. At the pump control panel, compare a sample of wiring against the diagram; flag any mismatch. 2. Check the CoC's panel reference against the pump control panel in the field, and check for signs of a modification since the CoC date. | 1. As-built wiring diagram for the pump control panel's electrical installation. 2. Current CoC for the pump control panel's electrical installation. | duplicates MEC-010 and MEC-009 scoped to a different panel; the same pair recurs at MEC-052, 064, 094 and 101 | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-090 | Mechanical | Sewer, Potable & Stormwater Pumps | Reliability | Duty/standby alternation, level alarms/telemetry, spill history, standby power, PM records. | Evidence + Site Physical Verification + Question | Asset | examine | Duty/standby setting, balanced run hours and a float switch fouled with rag are read at the panel and in the wet well. | 1. At the pump station control panel, check the duty/standby selector setting and, if displayed, the pump run-hours to see if they're roughly balanced between pumps. 2. Locate the level sensors/float switches in the wet well and check they're correctly positioned, clean and undamaged; check the telemetry panel shows a live, working connection. 3. Look around the pump station and surrounding ground for evidence of past overflow (staining, odour, distressed vegetation) that isn't accounted for in the spill register. 4. Locate the standby generator/power source for the station and check it's present, fuelled (if diesel) and shows evidence of recent testing. | Duty/standby alternating with roughly balanced run hours, level sensors clean and free, alarms confirmed through to IMC on the monthly cycle, standby power proven, and spill history with each event investigated. | evidence stub: 'PM & alarm records'
KSIA-MEC-091 | Mechanical | Gas Hot Water Facility | Gas Hot Water Facility | Sewer sump gas monitor calibration records | Evidence + Site Physical Verification | Document | reconcile | Read as written it is the same gas-monitor certificate check as MEC-086. | Physically check the gas monitor's serial number against the calibration certificate to confirm it's the actual unit used in the field (not a spare); check the monitor is configured to detect H2S, LEL and O2 as appropriate for a sewer environment. | Gas monitor calibration certificate for the confined-space gas detector(s) used for sewer sump entry. Daily bump-test records showing the monitor was checked before each entry. | WRONG SYSTEM: the requirement, evidence and walkabout all say SEWER SUMP and confined-space entry, filed under Gas Hot Water Facility. This is a copy of MEC-086 pasted into the wrong asset system. if a gas monitor is genuinely required at a gas hot water facility it would be for LPG/combustible gas, which is a different instrument and a different configuration from H2S/LEL/O2 | delete, or rewrite as an LPG gas-detection check and confirm against ACSA's hot water system task list first
KSIA-MEC-092 | Mechanical | Gas Hot Water Facility | Gas Hot Water Facility | Earth leakage test | Evidence + Site Physical Verification | Document | examine | As MEC-087, scoped to the gas hot water facility. | At the pump control panel, check for evidence the panel hasn't been modified since the last earth-leakage test without a re-test. | Earth-leakage trip test record for the pump motor/control panel circuits. | sixth of six near-identical earth-leakage rows | one earth-leakage check scoped by asset system
KSIA-MEC-093 | Mechanical | Gas Hot Water Facility | Gas Hot Water Facility | Records of inspections for Guarding of moving parts | Evidence + Site Physical Verification | Asset | examine | A fitted guard is seen. But this row's evidence describes PUMP couplings and shafts. | At each pump, visually check couplings/shafts for fitted, undamaged guards; check for any guard removed for maintenance access and not reinstated, or present but loose/damaged. | Guarding inspection record for pump couplings, shafts and other moving parts, itemised per pump. | evidence text says 'pump couplings, shafts' — copied from MEC-088 (Sewer Pumps) without re-scoping to what actually rotates in a gas hot water facility the acsaThreshold cited is from Air Handling Units (D080 025M cl. 4.4.5), a third unrelated system | rewrite against the approved contractor task list for System - Hot Water (HWS) rather than inheriting the pump text
KSIA-MEC-094 | Mechanical | Gas Hot Water Facility | Gas Hot Water Facility | Panel wiring diagram and COC validity check | Evidence + Site Physical Verification | Document | reconcile | As MEC-089, scoped to the gas hot water facility panel. | 1. At the pump control panel, compare a sample of wiring against the diagram; flag any mismatch. 2. Check the CoC's panel reference against the pump control panel in the field, and check for signs of a modification since the CoC date. | 1. As-built wiring diagram for the pump control panel's electrical installation. 2. Current CoC for the pump control panel's electrical installation. | fifth of five near-identical wiring-diagram-and-CoC rows | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-095 | Mechanical | Gas Hot Water Facility | LPG safety | LPG installation certificate of conformity, registered installer, leak tests, ventilation & signage, cylinder storage compliant. | Evidence + Site Physical Verification | Document | examine | A CoC from a registered LPG installer, plus leak test records. Ventilation, signage and cylinder storage are the visible half. | 1. Locate and check the CoC is displayed or available on file, and check the installation date/details match what's physically installed. 2. Check for any smell of gas or visible corrosion/damage at pipe joints as a secondary indicator. 3. Check ventilation openings/louvres at the LPG installation are clear and unobstructed, and confirm hazard signage is present and legible. 4. Physically inspect the cylinder storage area — cylinders upright and secured, stored in open/ventilated air, clear of ignition sources, and not exceeding the storage area's rated capacity. | LPG installation CoC naming a registered installer, leak test records, ventilation openings unobstructed, signage present, cylinders stored upright, secured and segregated, with the flammable store designed to SANS 10400 and SDS held close by. | evidence stub: 'CoC; inspection' this is the ONLY substantive check in the Gas Hot Water Facility system — the other four (091-094) are copy-pastes from other systems
KSIA-MEC-096 | Mechanical | Water Treatment Plant | Water Treatment Plant | HBA Exposure monitoring programme of staff | Evidence + Site Physical Verification + Question | Document | reconcile | An HBA reg 7 monitoring programme with results. The walk finds the staff rotated into exposure who were never scoped into it. | At the treatment plant, confirm staff whose roles expose them to raw sewage/effluent are actually covered by the monitoring programme, including any staff rotated through roles not originally scoped into it. | Documented monitoring programme with the procedure used and results, an OREP per homogeneous exposure group, covering every role actually exposed — including recent rotations.
KSIA-MEC-097 | Mechanical | Water Treatment Plant | Water Treatment Plant | Disposal requirements of HBA, Requirement for procedures and certificates from designated disposal sites | Evidence + Site Physical Verification + Question | Practice | examine | Not whether a procedure exists but whether decontamination is actually done and whether every disposal produced a manifest. The gap between the procedure and the practice is the check. | At the treatment plant, check for evidence that decontamination/disinfection is actually being carried out on equipment in contact with HBA waste (not just documented as a procedure), and check manifests exist for every disposal run. | Written decontamination and waste-handling procedures, a manifest and safe-disposal certificate for EVERY disposal in the period reconciled against the waste register, from a site with a current permit — and visible evidence decontamination is performed on equipment.
KSIA-MEC-098 | Mechanical | Water Treatment Plant | Water Treatment Plant | waste/maintenance contractor's contract contains provisions to comply with these Regulations (HBA) Regulations | Evidence + Site Physical Verification | Document | reconcile | A clause in a signed contract. The walk checks the party on site is the party in the contract. | Confirm the entity/personnel actually carrying out waste/maintenance work on site match the contracted party named in the agreement. | Signed contract carrying the HBA reg 17(f) clause and EMS 048 appended and signed before commencement, with the personnel actually working matching the contracted entity.
KSIA-MEC-099 | Mechanical | Water Treatment Plant | Water Treatment Plant | Measures to control exposure to HBAs | Evidence + Site Physical Verification | Practice | examine | The hierarchy of control is a way of working. PPE issued but not worn, and a ventilation cover left off, both fail it while the register says compliant. | At the treatment plant, check PPE actually available matches the correct type/grade for biological hazard exposure specified in the risk assessment; check engineering controls (covers, ventilation) are maintained, not degraded; check hygiene facilities (handwashing, showers) are in service. | Risk assessment, PPE of the correct grade for biological hazard actually available and in use, engineering controls in place and maintained, and hygiene facilities usable — with issue and inspection registers behind them. | no acsaThreshold — the control hierarchy has no stated criterion here
KSIA-MEC-100 | Mechanical | Water Treatment Plant | Water Treatment Plant | Maintenance of control measures by approved HBA Inspection Authority | Evidence + Site Physical Verification | Document | reconcile | An HBA reg 12(b) examination report by an approved inspection authority. The walk checks the report's scope covers every control installed. | At the treatment plant, check the engineering controls actually installed (covers, ventilation, containment) against what the examination report lists, confirming none are missing from scope. | Thorough examination report within 24 months, listing each engineering control — with nothing installed on site missing from its scope.
KSIA-MEC-101 | Mechanical | Water Treatment Plant | Water Treatment Plant | Wiring diagram and COC validity check | Evidence + Site Physical Verification | Document | reconcile | As MEC-089, scoped to the water treatment plant. | 1. Compare the wiring diagram against the plant's actual wiring. 2. Check the CoC against the plant's current configuration for signs of an un-certified modification/upgrade. | 1. As-built wiring diagram for the water treatment plant's electrical installation. 2. Current CoC for the water treatment plant's electrical installation. | fourth of five near-identical wiring-diagram-and-CoC rows | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-102 | Mechanical | Water Treatment Plant | Water Treatment Plant | Earth leakage test | Evidence + Site Physical Verification | Document | examine | As MEC-087, scoped to the water treatment plant. | At the pump control panel, check for evidence the panel hasn't been modified since the last earth-leakage test without a re-test. | Earth-leakage trip test record for the pump motor/control panel circuits. | sixth near-identical earth-leakage row | one earth-leakage check scoped by asset system
KSIA-MEC-103 | Mechanical | Water Treatment Plant | Water Treatment Plant | Compliance of Hazardous chemical substance storage areas | Evidence + Site Physical Verification | Asset | examine | Bund capacity against what is actually stored, and incompatible chemicals sharing a shelf, are both seen in the store. | At the chemical storage area, check SDS sheets on display/on file match the chemicals actually in use; check bunding/containment capacity visually against the volume of chemical actually stored; check incompatible chemicals (e.g. acids next to chlorine) aren't stored together; confirm PPE specified in the risk assessment is physically available at the point of use. | Bunding at least 110% of the largest container in it, SDS present and matching the chemicals actually held, ventilation and signage in place, and incompatibles segregated.
KSIA-MEC-104 | Mechanical | Water Treatment Plant | Water Treatment Plant | Demarcation of Noise Zones and requirements for hearing protection | Evidence + Site Physical Verification | Asset | examine | A sign is on a wall or it is not, and it either names the right protection or it does not. | Walk the plant areas identified in the AIA noise assessment as noise zones and physically check for signage present, legible, and correctly specifying the hearing protection required; check any area added/changed since the last noise assessment has since been signed. | Signage present, legible and specifying the required hearing protection in every area the AIA survey put at or above 85 dBA — including areas added or changed since that survey.
KSIA-MEC-105 | Mechanical | Water Treatment Plant | Water Treatment Plant | Noise monitoring requirement by an AIA according to SABS 083 | Evidence + Site Physical Verification | Document | reconcile | The same AIA noise survey as MEC-016. | Walk the plant rooms/noise areas named in the AIA report and check the noise-zone demarcation/signage on site matches what the report identifies; confirm the report covers the full facility, not only some plant rooms. | Current AIA occupational noise assessment report (SANS 10083 methodology), dated within the regulatory cycle. Identifies noise zones and any areas at/above the 85 dB(A) action level. | verbatim duplicate of MEC-016 — identical requirement, evidence and walkabout | delete; one site noise survey check, with demarcation as MEC-104
KSIA-MEC-106 | Mechanical | Water Treatment Plant | Water quality | Potable water sampled and tested per SANS 241 schedule; disinfection residuals; reservoir cleaning records. | Evidence + Site Physical Verification | Document | reconcile | SANS 241 is a laboratory schedule. A chlorine residual can be spot-read at a tap, but the compliance is the monthly series. | 1. Check sampling points are accessible and show signs of routine use. 2. If a handheld chlorine test kit/meter is available, a spot reading can be taken at a tap; otherwise check the on-site monitoring log/logger reading against the required range. 3. Where accessible, visually inspect the reservoir interior (via inspection hatch, if safe and permitted) for sediment or biological growth, and check the roof/access hatch is secure. | Monthly sampling and test results at FALE against the SANS 241 schedule, disinfection residuals within range, reservoir cleaning records — and sampling points on site that show signs of routine use. | evidence stub: 'Lab results; cleaning records'
KSIA-MEC-107 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | 6 monthly Façade and lifting equipment examination report | Evidence + Site Physical Verification | Document | reconcile | A DMR reg 18.6 thorough examination by a competent person from a registered entity. Rope and hook wear is visible, but the report's itemisation is the check. | At the façade access unit (BMU/davit/gondola), visually inspect ropes, hooks and sheaves where accessible for obvious wear or damage, and check the examination report itemises each safety-critical component rather than giving a generic "equipment OK" sign-off. | Six-monthly report itemising ropes, chains, hooks, sheaves, brakes and safety devices individually — not a generic pass — from a registered Lifting Machinery Entity.
KSIA-MEC-108 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | Annual Façade access and lifting equipment load test certificates | Evidence + Site Physical Verification | Document | reconcile | A load test certificate is read against the SWL stamped on the machine. Both halves are needed. | Check the certificate's stated test load against the equipment's SWL nameplate; confirm the inspector's ECSA registration and the entity's Lifting Machinery Entity registration are both verifiable, not just claimed. | Certificate within 12 months stating a test load consistent with the SWL nameplate, from an ECSA-registered inspector at a registered entity — both verifiable, not merely claimed.
KSIA-MEC-109 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | Façade access equipment user's checklist (Prior to use) | Evidence + Site Physical Verification + Question | Practice | reconcile | Pre-use checklists exist to be filled in before use. Batch-completed at month end they are a record of nothing, and only the dates and their storage location reveal that. | Check the checklist storage location/box at the equipment itself, and check dates/times on a sample of checklists for signs they were batch-completed after the fact rather than filled in prior to each use. | Completed checklists stored at the equipment, dated and timed one per use occasion, covering controls, safety devices, anchor points and harness attachment — with no evidence of retrospective batch completion.
KSIA-MEC-110 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | Register of façade access and lifting equipment | Evidence + Site Physical Verification + Question | Document | reconcile | A register is compliant when it matches the equipment on site in both directions — nothing decommissioned still listed, nothing new missing. | Physically check the equipment identification tags on site against the register entries, confirming no decommissioned units are still listed and no recently added equipment is missing. | Register listing each item with its SWL and last/next examination and load-test dates, reconciled both ways against the identification tags found on site.
KSIA-MEC-111 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | Proof of registration of the entity performing load tests with the DOL as a Lifting Machinery Entity | Evidence + Site Physical Verification | Document | reconcile | A DMR reg 19 registration is a document. The walk checks the entity doing the work is the entity registered, not a sub-contractor. | Check whether the entity actually carrying out the load-testing work on site is the same registered entity named on the registration proof, not an unregistered sub-contractor. | Current DoL Lifting Machinery Entity registration for the entity actually performing the load tests, with SHE File competencies submitted 14 days before work.
KSIA-MEC-112 | Mechanical | Façade Access & Lifting Equipment | Façade Access & Lifting Equipment | Proof of registration with ECSA of the Lifting Machinery Inspector | Evidence + Question | Document | none | An individual's ECSA registration under the Engineering Profession Act, plus their employment by a registered entity. Neither is observable on site. | — nothing to inspect on site | ECSA registration for the named inspector and evidence they are employed by the registered Lifting Machinery Entity that issued the certificates. | no walkabout text at all, correctly no acsaThreshold
KSIA-MEC-113 | Mechanical | Façade Access & Lifting Equipment | Statutory tests | Cradles, hoists, MEWPs load-tested 12-monthly by registered LMI; lifting tackle register; operator competency. | Evidence + Site Physical Verification | Document | reconcile | A roll-up of MEC-107, 108 and 110, adding operator competency. | 1. Check the load-test certificate/tag displayed on or near each cradle/hoist/MEWP, confirming it's current and matches the unit. 2. Physically inspect a sample of lifting tackle (slings, shackles) for a valid inspection tag/colour-code and check the item's condition — no visible damage, corrosion or deformation. 3. Ask the operator on duty to show their competency card/authorisation and confirm they're listed as trained for this specific equipment type. | A load-test certificate within twelve months displayed on or near each cradle, hoist and MEWP and matching the unit, issued by an ECSA-registered LMI at a DoL-registered Lifting Machinery Entity; a lifting tackle register with a valid inspection tag or colour code on each sling and shackle at the three-monthly cycle; and operator competency evidenced on the training register. | evidence stub: 'LMI certificates; register' duplicates MEC-107, MEC-108 and MEC-110 | keep only operator competency, which nothing else asks, and the displayed-tag check on cradles, hoists, MEWPs and lifting tackle
KSIA-CIV-001 | Civil | Markings | Markings | Markings should be maintained in a conspicuous condition, readily visible to aircraft in the air or manoevering on the ground | Evidence + Site Physical Verification | Asset | examine | The paint on the ground IS the check. A repaint log proves work happened, not that the marking is visible today. | Walk/drive the runway, taxiways and apron and visually inspect markings for fading, rubber/fuel staining, overgrowth or damage; where possible, repeat under aerodrome lighting at dusk/night. Pass = markings sharply visible with no obscuring contamination or vegetation; fail = any marking not clearly discernible at normal approach/taxi speed. | Every marking type legible at taxi/approach speed, no rubber, fuel, dust or vegetation obscuring it — plus the monthly inspection report and the CMMS repaint interval actually applied to each marking type.
KSIA-CIV-002 | Civil | Markings | Markings | Check Marking dimensions (including the spacing between markings ) e.g centre lines, touch-down Zone, Aiming points & Designation Points | Evidence + Site Physical Verification | Asset | reconcile | A measured stripe/gap against the approved as-built. Neither half decides it alone — the drawing without the tape measures nothing, the tape without the drawing has no standard. | 1. Physically measure (tape/wheel) a sample of centre line stripes and gaps along the runway and compare against the applicable figure for the runway's category/code. Pass = measured dimensions within the standard's tolerance; fail = stripes/gaps or width off-spec, e.g. from imprecise re-masking drift over repeat repaints. 2. Count the touchdown zone marking pairs and measure their spacing from the threshold; compare the count against the LDA band. Pass = pair count/spacing/rectangle dimensions match the applicable band; fail = pair count reflects an outdated LDA (e.g. after a threshold/declared-distance change) or dimensions off-spec. | Measured centre-line stripe/gap, TDZ pair count and spacing within tolerance of the approved as-built for THIS runway, and the as-built current for the declared distances in force. | no acsaThreshold — D060 009M defers dimensions to ICAO Annex 14 and the as-builts, so the figure lives in a drawing this register does not name
KSIA-CIV-003 | Civil | Markings | Markings | Check visiblity of markings | Evidence + Site Physical Verification | Asset | examine | Visibility is a condition of the asset. Nothing in a file can make a faded marking compliant. | From ground level and, where practicable, from a vehicle moving at a representative speed, check each marking type for legibility; note any obscured by rubber/fuel staining, fading, vegetation or dust/sand. Repeat spot-checks at night under aerodrome lighting if the marking scheme is used at night. Pass = markings clearly identifiable; fail = any marking not reliably identifiable. | - Most recent runway/taxiway/apron inspection checklist or report specifically noting marking visibility/condition - Photos from the last routine inspection - Any pilot-reported marking-visibility occurrence records | overlaps CIV-001 almost entirely — 001 is 'conspicuous condition', 003 is 'visibility' | merge into CIV-001
KSIA-CIV-004 | Civil | Markings | Markings | Check if correct color is used | Evidence + Site Physical Verification | Asset | examine | Colour is read off the pavement. The paint spec says what was bought, not what is on the ground after two years of jet blast. | Visually inspect a representative sample of each marking type against the required colour; check apron safety lines actually contrast with adjacent stand markings, and check mandatory instruction markings are true red/white, not faded to pink/orange. Pass = colours match spec and remain distinguishable; fail = off-white/cream paint, faded yellow, low-contrast safety lines, or faded mandatory markings. | White/yellow/red as prescribed per marking type, apron safety lines still contrasting against stand markings, mandatory markings true red — not faded to pink.
KSIA-CIV-005 | Civil | Markings | Markings | Check distance from reference item e.g Holding position from centeline, taxiway center from holding points | Evidence + Site Physical Verification | Asset | reconcile | A holding-position distance is a measurement against the approved design, not against a textbook figure. | Measure (or request a recent survey of) the actual distance from the runway centre line to each holding-position marking/taxiway holding point; compare against the approved design/AIP figure — do not compare against a generic textbook number. Pass = measured distance matches design; fail = distance is stale (e.g. left at an old value after a code-number or category upgrade) or no design figure is available to check against. | Surveyed or measured distance from runway centre line to each holding position equal to the approved design/AIP figure — and the as-built updated if the runway has been re-declared.
KSIA-CIV-006 | Civil | Markings | Markings | Check visibility,dimensions, colour & background of Mandatory Information Markings | Evidence + Site Physical Verification | Asset | examine | Same physical reading as 002/003/004, narrowed to mandatory instruction markings — where a fade is a runway incursion rather than an untidiness. | 1. Inspect mandatory instruction markings at runway-holding positions and NO ENTRY points for correct white-on-red colour/contrast, correct clearance (≥1 m) from adjacent lines, and correct centring/duplication for the taxiway's code letter. Pass = colour and position match spec; fail = faded contrast or drifted/incorrect offset from the holding line. 2. Inspect information markings for correct black-on-yellow presentation and check they are not confused with or overlapping mandatory instruction markings after ad-hoc repainting. Pass = clearly distinguishable and correctly coloured; fail = overlap/confusion with mandatory markings or incorrect colours. | 1. Mandatory marking/signage layout drawing for the runway-holding positions and NO ENTRY points, plus the most recent inspection record confirming colour, legibility and correct positioning relative to the holding-position line 2. Most recent inspection record confirming information marking colour/legibility and that it is not confused with mandatory instruction markings | bundles four attributes (visibility, dimensions, colour, background) into one pass/fail | keep as one — mandatory markings warrant their own check, but say in the requirement that it is the mandatory subset of 002/003/004
KSIA-CIV-007 | Civil | Markings | Compliance | Marking dimensions, colour, conspicuity and location comply; repainting programme; retro-reflectivity where applicable. | Evidence + Site Physical Verification + Question | Asset | examine | A roll-up of 001-006 plus the repainting programme. Nothing here is verified that is not verified above. | Cross-check overall marking condition against what was observed during the dimension/colour/visibility walkabouts elsewhere in this register; if retro-reflectivity test equipment is available on site, ask to see a reading taken. | A repainting programme in the CMMS showing the interval applied to EACH marking type — centre line monthly, runway edges bi-annually — worked to date, obstacles repainted tri-monthly, monthly inspection reports determining removal and repainting, and a retro-reflectivity reading where the equipment exists. Condition itself is CIV-001 to CIV-006. | evidence stub: 'Inspection; programme' duplicates CIV-001 through CIV-006 | delete the condition half; keep only 'repainting programme exists and the interval per marking type is being met', which is a Document check
KSIA-CIV-008 | Civil | Visual Aids | Visual Aids | Markings should be maintained in a conspicuous condition, readily visible to aircraft in the air or manoevering on the ground | Evidence + Site Physical Verification | Asset | examine | Word-for-word CIV-001, filed under Visual Aids instead of Markings. | Walk/drive the runway, taxiways and apron and visually inspect markings for fading, rubber/fuel staining, overgrowth or damage; where possible, repeat under aerodrome lighting at dusk/night. Pass = markings sharply visible with no obscuring contamination or vegetation; fail = any marking not clearly discernible at normal approach/taxi speed. | - Marking repaint/refurbishment log or work order history for the runway and taxiways, covering the last 12 months - Most recent daily/weekly pavement inspection records (TGM §8.5/§8.6) noting marking condition - Any night-time inspection or pilot/pilot report (PIREP) complaint log referencing marking visibility | exact duplicate of CIV-001 — same requirement text, same evidenceExpected, same walkabout | delete
KSIA-CIV-009 | Civil | Visual Aids | Visual Aids | Check visibility,dimensions, colour & background of Apron Markings | Evidence + Site Physical Verification | Asset | examine | Apron markings read on the stand, against the stand's design drawing and the aircraft type actually parking there. | Inspect a sample of stands for marking visibility, colour/contrast (including apron safety line contrast against stand markings), and check lead-in/lead-out line placement is consistent with the aircraft type currently using the stand. Pass = markings visible, correctly coloured and consistent with current stand use; fail = inconsistent widths/offsets across stands, or markings not updated after an aircraft type change. | Markings visible and correctly coloured, and lead-in/lead-out lines matching the aircraft type currently using the stand — a stand upgauged to a wide-body with the old lines still painted is the failure this catches.
KSIA-CIV-010 | Civil | Visual Aids | Visual Aids | Check for availability, illumination and direction of Mandatory intersection signs | Evidence + Site Physical Verification | Asset | examine | A sign is present, oriented and lit, or it is not. All three are seen. | Check each mandatory instruction sign for availability, red/white colour and panel condition, correct orientation for the direction of travel, and (for signs required to be illuminated) confirm the lamp/LED is functioning — ideally verified at night or via the maintenance log's illumination test record. Pass = sign present, legible, correctly oriented, and illuminated where required; fail = failed illumination, faded contrast, or wrong orientation. | Each mandatory sign present, red/white, panel undamaged, oriented for the direction of travel, and illuminated where the runway operates at night or below 800 m RVR. | conflicting threshold in the source: signage inspection Daily (D060 001M cl. 4.9.23) versus Monthly (D060 014M cl. 4.7.8)
KSIA-CIV-011 | Civil | Visual Aids | Signs & indicators | Signs, PAPI siting/frangibility, wind indicators, obstacle marking/lighting per design; obstacle survey current. | Evidence + Site Physical Verification + Question | Asset | examine | Frangibility and siting are physical. The obstacle survey behind it is a document, and that is the half that is not seen. | Walk the sign and PAPI locations and visually compare their positions against the design layout; check the PAPI structure and its mounts are of frangible (break-away) design; look around the runway approach and take-off areas for obstacles — cranes, new buildings, tall vegetation — that might not be reflected in the last obstacle survey. | Signs and PAPI sited as the design layout shows, the PAPI structure and its mounts of frangible break-away design, the annual PAPI flight calibration certificate current, wind indicators and obstruction lights checked daily, and a Technical Evaluation under D060 015M current for the 10 km radius with WGS-84 three-dimensional coordinates and SA-CAA approval correspondence for anything erected. | bundles four unrelated asset types — signs, PAPI, wind indicators, obstacle marking/lighting — plus a document (the obstacle survey) evidence stub: 'Inspection; obstacle survey' | split four ways: PAPI siting and frangibility (Asset); signs (already CIV-010); wind indicators (already CIV-012); obstacle survey currency within the 10 km radius (Document)
KSIA-CIV-012 | Civil | Wind Direction Indicator | Condition | Wind direction indicators present, illuminated, frangible, correct colour and condition. | Evidence + Site Physical Verification | Asset | examine | A windsock is judged by watching it move and by what stands between it and the pilot. | Physically inspect the windsock — check it is roughly the right size, not torn or badly faded, moves freely in the wind, is lit at night if required, and that nothing (trees, buildings, new structures) blocks the view of it or disturbs the airflow reaching it. | Sock the correct size, not torn or faded, swinging freely, lit if required, grass at its base under 20 cm, and no new structure or tree in the line of sight or disturbing the airflow. | evidence stub: 'Site inspection'
KSIA-CIV-013 | Civil | Runway | Runway | The surface is maintained in such a condition such as to prevent formation of harmful irregularities | Evidence + Site Physical Verification | Asset | examine | A rut is found by walking on it with a straightedge. The condition survey says where to look. | Walk/drive the runway (especially the touchdown zone and high-turn areas) looking, and where available using a straightedge, for ruts/depressions/humps; cross-check against the latest pavement condition survey and inspection records for any noted-but-unremediated irregularities. Pass = no hazardous irregularity found, or all findings have linked work orders showing remediation; fail = visually hazardous irregularity present with no corrective action on file. | No depression, hump or rut in the touchdown or high-turn areas that a straightedge shows outside tolerance, and every irregularity in the latest PCI survey either closed or carrying a live work order.
KSIA-CIV-014 | Civil | Runway | Runway | Pavement Bearing Strength | Evidence + Site Physical Verification | Document | reconcile | Bearing strength cannot be seen. The published PCR decides it; the walk only checks that the traffic on the pavement is the traffic the PCR was calculated for. | Observe the aircraft types/mix actually operating on the runway and cross-check against the ACR figures in the PCR report to confirm no aircraft type exceeds the published rating. | Current PCR report in the five-part coded format, and no aircraft type in the actual movement mix with an ACR above it.
KSIA-CIV-015 | Civil | Runway | Runway | Provision of RESA at runway ends | Evidence + Site Physical Verification | Asset | reconcile | RESA is ground you can walk. Whether there is enough of it is a measurement against the declared distances. | Walk or drive out each RESA and, where a survey/design drawing is available, compare its actual length/width against the required figures; check visually for encroaching objects, vegetation, standing water or uneven ground that would impair deceleration. Pass = RESA meets minimum dimensions and is clear/functional; fail = falls short of minimum with no documented deviation/exemption, or is encroached/poorly maintained. | Measured RESA length and width at each end meeting the figure in the declared-distance calculation, clear of encroaching objects, standing water and uneven ground.
KSIA-CIV-016 | Civil | Runway | Runway | Surface Defects e.g Cracks , Rutting , Depression, Shoving e.t.c | Evidence + Site Physical Verification | Asset | examine | Cracking, rutting, depression and shoving are seen and severity-rated on the pavement. | Walk the runway looking for visible cracking, rutting, depression or shoving; note any that appear visually significant and check whether it has a corresponding structural-investigation record. Pass = no conspicuous undocumented distress found and survey within the recommended cycle; fail = conspicuous distress present with no triggered investigation, or survey overdue/incomplete. | No conspicuous distress on the pavement that is absent from the latest survey, and the survey itself within its three-yearly cycle. | overlaps CIV-025, which asks the same question with the PCI survey as its evidence
KSIA-CIV-017 | Civil | Runway | Runway | Oppotunistic Defects - Ponding , loose aggregates, vegetation growth in cracks e.t.c | Evidence + Site Physical Verification | Asset | examine | Ponding, loose aggregate and vegetation in joints are transient conditions — a record of a clean surface last month proves nothing about today. | 1. Inspect the surface after rainfall (or review recent post-rainfall photos/records) for pooled water; visually estimate depth and area affected against the 25%/3 mm threshold. Pass = no area meets the standing-water definition; fail = ponding meeting or exceeding the threshold, especially if recurring at the same low spots (possible drainage/grading defect). 2. Inspect cracks/joints and surface for loose aggregate (ravelling) and vegetation growth; check the maintenance log for clearing frequency. Pass = no loose aggregate/vegetation present, or all within a documented recent clearing cycle; fail = vegetation/aggregate visibly present with no recent clearing record. | No area meeting the standing-water definition after rain, no loose aggregate that could become FOD, and no vegetation in joints beyond the 30 cm herbicide band.
KSIA-CIV-018 | Civil | Runway | Runway | Edge of Runway flush with surrounding areas | Evidence + Site Physical Verification | Asset | examine | A lip at the pavement edge is felt underfoot and measured with a straightedge. | Walk the runway edge at representative points, visually and (if available) with a straightedge/measuring tool, checking for a step or lip at the pavement/shoulder interface. Pass = no discernible step/lip; fail = a measurable step, especially if not tracked against any documented tolerance (note: no SACAA numeric tolerance exists, so use the aerodrome's own adopted standard if one exists). | No measurable step between pavement and shoulder at representative points — and, first, a documented tolerance to measure against. | no threshold anywhere in the source for how big a step is a failure — the check has no pass mark
KSIA-CIV-019 | Civil | Runway | Runway | Asphalt Edge breaks | Evidence + Site Physical Verification | Asset | examine | Crumbling asphalt at the edge is seen, and the fragments are the FOD source. | Walk the pavement edge looking for crumbling/broken asphalt, particularly where the shoulder has eroded or settled; check for loose fragments that could become FOD. Pass = no significant edge deterioration, or defects tracked with a documented severity trend; fail = visible edge breaks with no severity tracking or shoulder-support assessment on file. | - Recent pavement condition survey noting edge-break locations and severity - Shoulder construction/maintenance standard ACSA applies (to assess whether edge support is adequate by design) | overlaps CIV-016 (surface defects) and CIV-018 (edge flush) — three checks walking the same 10 cm of pavement | fold into CIV-018 as the edge check
KSIA-CIV-020 | Civil | Runway | Runway | Runway slopes | Evidence + Site Physical Verification | Document | reconcile | A longitudinal slope is not judgeable by eye. The as-built or survey profile decides; the walk only finds local flat spots and reverse grades at patches. | Request/compare the runway's as-built or design survey profile against the applicable code-based slope limits; visually check for localised flat spots or reverse grades at pavement joints/patches that could disrupt drainage even where the overall slope is compliant. Pass = current survey confirms slopes within limits; fail = no current as-built survey available, or reference code changed without re-checking slope compliance. | Current survey profile within the code-based longitudinal and transverse limits, and no localised reverse grade at a joint or patch holding water.
KSIA-CIV-021 | Civil | Runway | Runway | Check adequacy of Dimensions & Grading of Safety Areas for each runway | Evidence + Site Physical Verification | Asset | reconcile | The graded strip is walked and compared against the design width; encroachment is the failure and it is visible. | Walk/drive the graded strip either side of the runway, checking against the design drawing for width/length, and look for encroachment by fencing, drainage infrastructure, service roads or vegetation. Pass = graded extent matches design and is unobstructed; fail = encroachment present, or no current survey exists to confirm the design boundary is still met. | Graded extent matching the design drawing for the runway's code number, grass under 20 cm across the 50 m band, and no fencing, drainage or service road inside the graded width.
KSIA-CIV-022 | Civil | Runway | Runway | Strength of Strip Areas | Evidence + Site Physical Verification | Document | examine | Strip bearing capacity is a geotechnical number. The walk can only find seasonal softness a dry-season CBR would miss. | This is largely a document-based check, but during the walkabout visually assess the strip's ground condition (softness, saturation, rutting from vehicle use), especially in wet conditions, since a dry-season inspection can miss seasonal weakness. Pass = ground visually firm/trafficable and supported by geotechnical documentation; fail = visibly soft/saturated ground with no supporting test data, or no geotechnical report available at all. | CBR results or a geotechnical report for the graded strip showing it will carry an RFF vehicle, and ground visibly firm at the time of the audit. | no acsaThreshold and no ACSA evidence named at all — the CBR figure and the RFF trafficability standard are not in the register
KSIA-CIV-023 | Civil | Runway | Runway | Check Frangibility objects in Safety areas and Presence of Illegal Objects | Evidence + Site Physical Verification | Asset | reconcile | Every object in the strip is counted on the ground and matched to a register that says it is frangibly mounted. An unregistered object is the finding. | 1. Walk the strip/RESA identifying every object present (lights, wind cones, signage, poles); check each against an object register for frangible-mount certification, and visually assess mounting height/rigidity. Pass = every object accounted for in a register with frangibility confirmed; fail = an object present without a frangibility assessment, or no register exists to check against. 2. Walk the strip/RESA looking for anything not on the object register and not clearly serving a navigation/safety function — parked maintenance vehicles, stored materials, temporary construction equipment, informal access tracks. Pass = no unauthorised object present; fail = any unauthorised object found during the walk-down. | 1. Inventory/register of all objects sited within the runway strip and RESA (light fittings, wind cones, signage, poles) noting their frangible-mount certification or design compliance 2. Most recent safety-area walk-down/inspection record checking for unauthorised objects | two different checks in one: frangibility of authorised objects, and the presence of unauthorised ones | split in two — frangible-mount certification of every registered object (Asset/reconcile), and a clear-strip sweep for unauthorised objects (Asset/examine)
KSIA-CIV-024 | Civil | Runway | Friction | Runway friction (CFME) tested at required frequency; results above maintenance-planning level; corrective action (rubber removal/retexturing) where below. | Evidence + Site Physical Verification + Question | Document | examine | A friction coefficient cannot be seen. The signed CFME report is the only thing that decides it; rubber build-up in the touchdown zone is a hint, not a reading. | During the walkabout, look at the touchdown zone for rubber build-up, a polished or glazed appearance, or visible contamination — signs that friction may be reduced there — and confirm these areas are covered by the friction survey. The actual friction value cannot be judged by eye; rely on the test report for the pass/fail determination. | Signed friction results for RWY 06/24 at the three-monthly interval, tested at 1 mm self-wetting with a smooth tread tyre, every section above the maintenance planning level — or a corrective-action record where it was not. | evidence stub: 'Friction test reports; action records' overlaps CIV-026 almost exactly
KSIA-CIV-025 | Civil | Runway | Surface condition | Pavement condition (PCI) survey; cracking, spalling, joint sealant, rutting, FOD generation; repairs programmed. | Evidence + Site Physical Verification | Document | examine | The PCI survey is the instrument; the walk cross-checks it. But 016, 017 and 019 already walk the same defects. | Walk the runway looking for visible cracking, spalling, deteriorated joint sealant, rutting, and loose material that could become FOD; compare what you see against what the survey recorded, and flag anything visibly serious that isn't in the survey or has no linked repair record. | A PCI survey to ASTM D5340 within the three-yearly cycle, every distress it records carrying a programmed repair or a closed work order, concrete apron joint material replaced on the five-yearly cycle, and nothing visibly serious on the pavement that is absent from the survey. | evidence stub: 'PCI survey; work orders' overlaps CIV-016, CIV-017 and CIV-019 | keep as the document check — 'PCI survey current within 3 years and every distress it records carries a programmed repair' — and let 016/017/019 carry the condition
KSIA-CIV-026 | Civil | Friction Measurement & Corrective Maintenance | Friction Measurement & Corrective Maintenance | measurements of friction charecteristics of a runway surface and corrective maintenance when the friction charecteristics are below minimum friction levels | Evidence + Site Physical Verification | Document | examine | Same instrument, same report, same decision as CIV-024. | Primarily a document-based check against survey data; during the walkabout, visually note rubber-contaminated or visibly polished/glazed sections of the touchdown zone that commonly correlate with reduced friction, and confirm these are included in the friction survey coverage. Pass = latest survey results meet minimum thresholds, or below-threshold sections have documented corrective action; fail = below-minimum results with no corrective maintenance record, or survey coverage misses high-risk sections. | - Most recent continuous friction-measuring survey report for each runway, showing measured Mu values by section against the design objective, maintenance planning, and minimum friction levels for the specific device/tyre combination used - Records of any corrective maintenance (e.g. rubber removal, grooving) triggered by low readings | duplicates CIV-024 — one is under Runway/Friction, the other under its own asset system | merge with CIV-024
KSIA-CIV-027 | Civil | Friction Measurement & Corrective Maintenance | Friction Measurement & Corrective Maintenance | Is friction measured based on the latest Aircraft Movement for the Airport | Evidence | Document | none | Movement statistics against Table A's traffic ladder. Purely a reconciliation of two records — nothing on the airfield changes the answer. | — nothing to inspect on site | Average daily turbo-jet arrivals per runway end, the Table A band that number falls in, and test dates showing that interval actually applied — plus a Z001 003M change record if traffic moved the band. | no walkabout text at all, correctly
KSIA-CIV-028 | Civil | Friction Measurement & Corrective Maintenance | Friction Measurement & Corrective Maintenance | Records of Friction Testing Results | Evidence | Document | none | The existence and completeness of the record register is the check. | — nothing to inspect on site | Register covering 2-3 years with date, runway end, device and tyre, measured Mu by section, and the corrective-action reference — each signed off within two weeks and retained five years. | no walkabout text at all, correctly overlaps CIV-024, whose evidence is the same reports
KSIA-CIV-029 | Civil | Friction Measurement & Corrective Maintenance | Friction Measurement & Corrective Maintenance | Analysis of Friction Testing resuts and Corrective measures (if any) | Evidence + Question | Practice | none | Not whether a report exists but whether a below-threshold reading actually PRODUCES rubber removal, a re-test and, at minimum level, a NOTAM. That loop either runs or it does not. | — nothing to inspect on site | For each reading at or below the maintenance planning level, a corrective work order, the treatment record, and a post-treatment re-test above the level — and for any at or below minimum, the NOTAM. | no walkabout text at all
KSIA-CIV-030 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | The surface is maintained in such a condition such as to prevent formation of harmful irregularities | Evidence + Site Physical Verification | Asset | examine | Same physical reading as CIV-013, on the taxiway. | Walk/drive the taxiway, especially heavily-trafficked turning/junction areas, looking, and where available using a straightedge, for ruts/depressions/humps; cross-check against the latest pavement condition survey and inspection records for any noted-but-unremediated irregularities. Pass = no hazardous irregularity found, or all findings have linked work orders showing remediation; fail = visually hazardous irregularity present with no corrective action on file. | - Latest pavement condition survey report (Pavement Condition Index (PCI)/visual condition survey) for the taxiway - Weekly/annual inspection records (TGM §8.5–§8.7) noting any surface irregularity findings and remedial work orders raised | identical requirement text to CIV-013 and CIV-039 — the register repeats the pavement condition set once per surface type | consider one pavement-condition check scoped to a surface, rather than three identical checks
KSIA-CIV-031 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Pavement Bearing Strength, Taxiway strength to be equal to that of Runways | Evidence + Site Physical Verification | Document | reconcile | As CIV-014, for the taxiway. The PCR decides; the walk notes push-back and turning areas the evaluation must have allowed for. | Primarily a document-based check against the taxiway-specific PCR report; during the walkabout, note any signs of unusually concentrated or heavy loading (e.g. push-back/turning areas) that should be reflected in the bearing-strength evaluation. | Taxiway-specific PCR report and no ACR in the using traffic above it. | requirement asserts 'taxiway strength to be equal to that of runways' with no source named for that rule
KSIA-CIV-032 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Surface Defects e.g Cracks , Rutting , Depression, Shoving e.t.c | Evidence + Site Physical Verification | Asset | examine | Same physical reading as CIV-016, on the taxiway. | Walk the runway looking for visible cracking, rutting, depression or shoving; note any that appear visually significant and check whether it has a corresponding structural-investigation record. Pass = no conspicuous undocumented distress found and survey within the recommended cycle; fail = conspicuous distress present with no triggered investigation, or survey overdue/incomplete. | - Most recent detailed pavement condition/structural survey report (PCI or equivalent) showing crack, rut, depression and shoving severity by pavement section - Evidence of the routine visual inspection cycle (ideally not exceeding 3 years) feeding into it | walkabout text says 'Walk the runway' — copied from CIV-016 and not re-scoped duplicates CIV-016 and CIV-041
KSIA-CIV-033 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Oppotunistic Defects - Ponding , loose aggregates, vegetation growth in cracks e.t.c | Evidence + Site Physical Verification | Asset | examine | Same transient condition as CIV-017, on the taxiway. | 1. Inspect the surface after rainfall (or review recent post-rainfall photos/records) for pooled water; visually estimate depth and area affected against the 25%/3 mm threshold. Pass = no area meets the standing-water definition; fail = ponding meeting or exceeding the threshold, especially if recurring at the same low spots (possible drainage/grading defect). 2. Inspect cracks/joints and surface for loose aggregate (ravelling) and vegetation growth; check the maintenance log for clearing frequency. Pass = no loose aggregate/vegetation present, or all within a documented recent clearing cycle; fail = vegetation/aggregate visibly present with no recent clearing record. | 1. Photographic or written evidence from recent inspections of ponding locations after rainfall 2. Vegetation control / crack-sealing maintenance log showing frequency of clearing loose aggregate and vegetation from joints and cracks | duplicates CIV-017 and CIV-042
KSIA-CIV-034 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Edge of Taxiway flush with surrounding areas | Evidence + Site Physical Verification | Asset | examine | A step at the taxiway/apron junction is where construction dates meet; it is found on foot. | Walk representative taxiway edge sections, particularly at taxiway/apron junctions where pavement types or construction dates differ, checking for a step or lip. Pass = no discernible step; fail = a measurable step, especially where narrower/less robust taxiway shoulders show settlement. | - Taxiway shoulder/edge inspection records - Measured survey of pavement-to-shoulder level difference at representative taxiway sections, if available | no threshold for the size of a failing step, same as CIV-018
KSIA-CIV-035 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Asphalt Edge breaks | Evidence + Site Physical Verification | Asset | examine | Same as CIV-019, on the taxiway. | Walk the pavement edge looking for crumbling/broken asphalt, particularly where the shoulder has eroded or settled; check for loose fragments that could become FOD. Pass = no significant edge deterioration, or defects tracked with a documented severity trend; fail = visible edge breaks with no severity tracking or shoulder-support assessment on file. | - Recent pavement condition survey noting edge-break locations and severity - Shoulder construction/maintenance standard ACSA applies (to assess whether edge support is adequate by design) | duplicates CIV-019 | fold into CIV-034
KSIA-CIV-036 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Taxiway slopes allow for drainage | Evidence + Site Physical Verification | Asset | examine | Whether the slope drains is answered by looking at the taxiway after rain — unlike the runway's longitudinal profile, this one IS visible. | Inspect the taxiway after rainfall (or review post-rainfall records/photos) for ponding; where a design cross-section is available, compare against it. Pass = no ponding and slope consistent with design; fail = ponding present despite a compliant design slope (suggesting a downstream blockage) or no design cross-section available to check against. | No ponding after rainfall; where there is ponding on a design-compliant cross-section, a downstream blockage identified and a work order raised within the same operational day.
KSIA-CIV-037 | Civil | Taxiways & Taxilanes | Taxiways & Taxilanes | Check adequacy of Dimensions & Grading of Safety Areas for the Code of the Associated Taxiway | Evidence + Site Physical Verification | Asset | reconcile | As CIV-021, for the taxiway strip against its code letter. | Walk the graded strip either side of the taxiway; compare against the design drawing for the taxiway's code letter, checking for encroachment by fencing, lighting infrastructure or vegetation. Pass = graded extent matches design and is unobstructed; fail = encroachment present, code letter reclassified upward without widening, or no current survey available. | - Taxiway design layout drawing showing graded strip width for its aerodrome reference code letter - Recent survey confirming actual graded extent and freedom from obstructing objects | duplicates CIV-021
KSIA-CIV-038 | Civil | Taxiways & Taxilanes | Surface condition | Taxiway/taxilane pavement condition, edge drop-offs, shoulders, joint sealing; centreline markings. | Evidence + Site Physical Verification | Asset | examine | A roll-up of 030-037 with nothing new in it. | Walk representative taxiway sections looking specifically for any unsafe condition — one that could affect aircraft handling or generate FOD — that hasn't already been flagged in the specific pavement/edge/marking checks above. | Monthly taxiway and taxilane inspection plus the three-yearly visual assessment, manoeuvring areas inspected at least three times a week, concrete joint material replaced five-yearly, and no unsafe condition on the walk — one that could affect aircraft handling or generate FOD — that is not already recorded against a specific check. | evidence stub: 'Inspection reports' duplicates CIV-030, 032, 034, 035 and the taxiway centreline marking is already CIV-001/003 | delete
KSIA-CIV-039 | Civil | Aprons | Aprons | The surface is maintained in such a condition such as to prevent formation of harmful irregularities | Evidence + Site Physical Verification | Asset | examine | Same physical reading as CIV-013, on the apron. | Walk/drive the apron, especially heavily-trafficked stand and turning areas, looking, and where available using a straightedge, for ruts/depressions/humps; cross-check against the latest pavement condition survey and inspection records for any noted-but-unremediated irregularities. Pass = no hazardous irregularity found, or all findings have linked work orders showing remediation; fail = visually hazardous irregularity present with no corrective action on file. | - Latest pavement condition survey report (Pavement Condition Index (PCI)/visual condition survey) for the apron - Weekly/annual inspection records (TGM §8.5–§8.7) noting any surface irregularity findings and remedial work orders raised | duplicates CIV-013 and CIV-030
KSIA-CIV-040 | Civil | Aprons | Aprons | Pavement Bearing Strength, Apron strength to be equal to that of Runways | Evidence + Site Physical Verification | Document | reconcile | As CIV-014, for the apron — with the added point that a stand carries a static load a rolling evaluation may not cover. | Primarily a document-based check against the apron-specific PCR report; during the walkabout, note whether a wide-body or heavier aircraft type now regularly parks at a stand that was designed/rated for a lighter aircraft. | Apron PCR report whose method accounts for static parking loads, and no stand routinely taking an aircraft heavier than its rating.
KSIA-CIV-041 | Civil | Aprons | Aprons | Surface Defects e.g Cracks , Rutting , Depression, Shoving e.t.c | Evidence + Site Physical Verification | Asset | examine | Same physical reading as CIV-016, on the apron. | Walk the runway looking for visible cracking, rutting, depression or shoving; note any that appear visually significant and check whether it has a corresponding structural-investigation record. Pass = no conspicuous undocumented distress found and survey within the recommended cycle; fail = conspicuous distress present with no triggered investigation, or survey overdue/incomplete. | - Most recent detailed pavement condition/structural survey report (PCI or equivalent) showing crack, rut, depression and shoving severity by pavement section - Evidence of the routine visual inspection cycle (ideally not exceeding 3 years) feeding into it | walkabout text says 'Walk the runway' — copied from CIV-016 and not re-scoped duplicates CIV-016 and CIV-032
KSIA-CIV-042 | Civil | Aprons | Aprons | Oppotunistic Defects - Ponding , loose aggregates, vegetation growth in cracks e.t.c | Evidence + Site Physical Verification | Asset | examine | Same transient condition as CIV-017, on the apron. | 1. Inspect the surface after rainfall (or review recent post-rainfall photos/records) for pooled water; visually estimate depth and area affected against the 25%/3 mm threshold. Pass = no area meets the standing-water definition; fail = ponding meeting or exceeding the threshold, especially if recurring at the same low spots (possible drainage/grading defect). 2. Inspect cracks/joints and surface for loose aggregate (ravelling) and vegetation growth; check the maintenance log for clearing frequency. Pass = no loose aggregate/vegetation present, or all within a documented recent clearing cycle; fail = vegetation/aggregate visibly present with no recent clearing record. | 1. Photographic or written evidence from recent inspections of ponding locations after rainfall 2. Vegetation control / crack-sealing maintenance log showing frequency of clearing loose aggregate and vegetation from joints and cracks | duplicates CIV-017 and CIV-033
KSIA-CIV-043 | Civil | Aprons | Aprons | Edge of Apron flush with surrounding Safety areas | Evidence + Site Physical Verification | Asset | examine | The apron edge meets four different surrounding types and each boundary is walked. | Walk the apron perimeter, checking each boundary type (grass safety strip, service road, taxilane) for a step or lip, including drainage channels running along the edge that could create a level discontinuity. Pass = no discernible step; fail = a step present, particularly where ground support equipment traffic causes edge wear, or apron edge condition isn't covered by the standard movement-area inspection scope. | - Apron edge/perimeter inspection records - Confirmation of the surrounding area type (grass safety strip, service road, taxilane) the apron edge adjoins at each boundary | duplicates CIV-018 and CIV-034
KSIA-CIV-044 | Civil | Aprons | Aprons | Corner breaks & Joint sealant failure | Evidence + Site Physical Verification + Question | Asset | examine | A corner break is a triangular crack in a concrete slab — the one distress on this register that is genuinely apron-specific and not a repeat. | 1. Walk concrete slab pavement (apron) checking slab corners for cracks intersecting joints and isolating a triangular piece; note severity (extent of displacement/looseness). Pass = no corner breaks, or all identified and severity-classified in the survey; fail = corner breaks present without severity classification or a referenced distress standard. 2. Inspect slab joints for cracked, missing or extruded sealant; check whether resealing is logged as a scheduled maintenance item rather than ad-hoc housekeeping. Pass = sealant intact or a documented resealing programme is in place; fail = visibly failed sealant with no resealing programme, risking accelerated corner-break damage. | No corner break or failed joint sealant absent from the survey, and concrete joint material replaced on the five-yearly cycle.
KSIA-CIV-045 | Civil | Aprons | Condition & contamination | Apron surface condition, joint sealant, fuel/oil contamination, spillage clean-up procedure, tie-down/grounding points. | Evidence + Site Physical Verification + Question | Asset | examine | Fuel staining and a broken grounding point are seen on the stand. But the spill-response procedure bundled in with them is a practice, and the separator test is a document. | Walk a sample of stands checking for oil/fuel staining on the pavement, joint sealant condition, and the physical presence and condition of tie-down rings and aircraft grounding points — check they are not broken, corroded, or missing. | Stand pavement sound with joint sealant intact, no fuel or oil staining, tie-down rings and aircraft grounding points present, unbroken and uncorroded — plus a spill response procedure with containment inside 2 hours, oil separators tested annually for efficiency, sludge depth under 25% of chamber depth and disposal records retained 5 years. | evidence stub: 'Inspection; spill records' three different check types in one: surface condition (Asset), spill clean-up procedure (Practice), tie-down and grounding point condition (Asset) | split the spill-response half out as a Practice check — 2-hour containment, disposal records retained 5 years — and leave condition and grounding points as the Asset check
KSIA-CIV-046 | Civil | Pavement Strength | Pavement Strength | Report on Pavement Bearing strength on completion of construction or after major repair work | Evidence + Site Physical Verification | Document | reconcile | Whether a reassessment was TRIGGERED is a document question; the walk only establishes that works happened that should have triggered it. | Note the location and extent of any recent repair/construction work on site as context for whether a bearing-strength reassessment should have been triggered. | For every major repair or construction in the period, a post-works PCR reassessment, a pre-return-to-service friction verification, and the updated figure submitted to the AIP.
KSIA-CIV-047 | Civil | Pavement Strength | Strength rating | PCN published and supported by current pavement evaluation; overload approvals controlled. | Evidence + Site Physical Verification + Question | Document | reconcile | The published rating and the evaluation behind it are documents; the walk notes whether real traffic still matches. | Note the aircraft types actually operating at stands/on the movement area as a rough cross-check that the published pavement strength rating still matches real-world traffic. | A published pavement strength rating supported by a current evaluation and matching the AIP entry, with a controlled approval on file for every overload operation. NOTE: the check says PCN, which ICAO replaced with PCR — read it as the PCR published under CIV-014. | evidence stub: 'Pavement evaluation; AIP entry' says PCN, which ICAO replaced with PCR — the register is on the old vocabulary here while CIV-014 uses PCR duplicates CIV-014 and CIV-046 | merge into CIV-014, keeping only the overload-approval control as its own line
KSIA-CIV-048 | Civil | Rubber Removal & Contaminants | Rubber Removal & Contaminants | Remove contaminants as rapidly as posible and completely as posible | Evidence + Site Physical Verification | Practice | examine | The requirement is 'as rapidly as possible' — a response time, not a condition. The build-up you see is evidence the practice is not running. | 1. Inspect the touchdown zone for rubber deposit buildup (dark glazed patches); cross-check against the removal work order log for method used, area treated and elapsed time from detection to completion. Pass = no excessive buildup, or buildup is scheduled/being addressed per the log; fail = visible heavy rubber buildup with no recent removal record. 2. Check apron/stand areas for any residual sand or spill staining left from a cleanup; review incident/spill reports for response-time documentation. Pass = no residual sand/spill material found and spill records show prompt response; fail = sand or spill residue observed on the surface, or spill response time not documented. | Removal log showing elapsed time from detection to completion against the friction trigger, the method used, and a post-treatment friction result back above the maintenance planning level.
KSIA-CIV-049 | Civil | FOD Management | FOD Management | Remove FOD on Runways, Taxiways and Aprons | Evidence + Site Physical Verification | Practice | examine | FOD is cleared continuously or not at all; a clean runway on audit day proves the sweep ran this morning, nothing more. The programme and its coverage are the check. | Walk representative sections of runway, taxiway and apron looking for FOD (loose debris, bags, paper, sand, rubble); check for consistent sweep coverage across all three surface types, not just the runway. Pass = no FOD found, or sweep log shows recent complete coverage; fail = FOD present, or sweep records exist for the runway but show gaps for taxiways/apron. | FOD Management Programme document, sweep log covering runway, taxiway AND apron with location, date, time and nature of each item, bins inspected twice daily and emptied at three-quarters, and FOD in induction training records.
KSIA-CIV-050 | Civil | Drainage | Drainage | Ensure none of the drains are blocked and ensure drainage structures perform the tasks they were designed for | Evidence + Site Physical Verification | Asset | examine | A blocked catchpit is seen by lifting the lid. Silt and vegetation are conditions of the asset. | Inspect accessible drainage features (open drains, catchpits, culvert outlets) for silt, debris or vegetation build-up reducing capacity; where possible, check post-heavy-rainfall inspection records for structures that performed as designed. Pass = no visible blockage and schedule covers the full system; fail = blockage found, or schedule leaves remote/less-visible drains (e.g. under taxiways, along the Runway End Safety Area (RESA)) unchecked for extended periods. | No visible blockage in accessible drains, catchpits and culvert outlets; the cleaning schedule covering every airside drainage asset group; and blocked inlets on a runway or taxiway closed within 2 hours.
KSIA-CIV-051 | Civil | Drainage | Airside drainage | Stormwater drains, culverts and channels clear; inspection register; oil/water separators serviced; no ponding on movement areas. | Evidence + Site Physical Verification | Asset | examine | The drains are the same drains as CIV-050. The separator servicing bundled in is a document check with a laboratory result behind it. | Inspect accessible drainage features (open drains, culvert outlets, catchpits) for silt, debris or vegetation blocking flow; locate the oil/water separator(s) and look for signs of poor maintenance (overflow staining, odour, an oily sheen); check the runway, taxiway and apron surfaces for ponding, especially if it has rained recently. | Stormwater drains, culverts and channels clear of silt, debris and vegetation with an inspection register covering every airside drainage asset group; oil/water separators tested annually for efficiency with sludge depth under 25% of chamber depth and hazardous waste disposal at a licensed facility recorded and retained 5 years; and no ponding on any movement area. | evidence stub: 'Inspection register' duplicates CIV-050 for the drains; overlaps CIV-017/033/042 for the ponding | keep only the oil/water separator half and make it a Document check — annual efficiency test, sludge depth under 25% of chamber depth, disposal records retained 5 years
KSIA-CIV-052 | Civil | Inspections | Inspections | Daily , Weekly, Annual and Special inspections | Evidence + Site Physical Verification | Practice | reconcile | Not whether a log exists but whether the rounds actually happen at the stated frequency — which is why the walkabout says shadow one. | 1. Review the daily inspection log for the audit period and count entries per day; if practical, observe or shadow one inspection round in progress. Pass = ≥3 logged inspections every day with no unexplained gaps; fail = days with fewer than 3 inspections and no documented reason or catch-up inspection. 2. Request the weekly inspection record and, during the walkabout, check the named high-load areas (departure taxiways, stands, take-off taxiways, intersections, touchdown zones) for evidence of recent detailed inspection (e.g. chalk marks, freshly noted findings). Pass = weekly record demonstrably covers and emphasises the named high-load areas; fail = weekly record generic, with no clear focus on those areas. 3. Check whether the current annual inspection report's scope still covers all pavements presently in use, with no new/expanded areas omitted. 4. During the walkabout, check for any recently cut grass areas and confirm clippings have been fully removed (a specific §8.8.3 trigger); request the most recent special inspection records tied to any recent complaint, construction activity or unusual event and check team composition. Pass = special inspections documented for all applicable trigger events with qualified personnel; fail = a trigger event (e.g. recent grass cutting) with no corresponding special inspection record, or no evidence of qualified personnel on the team. | Three logged manoeuvring-area inspections every day with no unexplained gap, the apron audit twice a month, the bay inspection daily during turnaround, and the most recent annual inspection signed by a qualified civil engineer.
KSIA-CIV-053 | Civil | Inspections | Inspections | Availability of Inspection programme & Procedure | Evidence + Question | Document | none | The existence of a written programme and procedure, with responsibilities and defect-correction timeframes named in it. | — nothing to inspect on site | The documented inspection programme and procedure in the Aerodrome Manual or SMS, naming who inspects what at what interval and the timeframe for correcting each defect priority. | no walkabout text at all, correctly
KSIA-CIV-054 | Civil | Inspections | Serviceability inspections | Daily movement-area serviceability inspections logged; defects reported and closed; wildlife/FOD reports. | Evidence + Site Physical Verification + Question | Practice | reconcile | Whether defects raised in the log are actually closed on the ground. That closure loop is the practice. | Ask to see today's (or the most recent) daily inspection log entry, and check whether defects noted in recent entries are visibly being addressed or already fixed on site. | A daily movement-area serviceability log with today's entry present, checklists forwarded daily to the responsible Manager and audited by them, every defect raised carrying an Oracle eAM work request with a Date of Call, and the recent defects visibly fixed or in progress on site — plus wildlife and FOD reports for the period. | evidence stub: "Inspection logs" duplicates CIV-052 for the daily inspection frequency | keep only the defect-closure loop; the frequency is CIV-052
KSIA-CIV-055 | Civil | Airside Service Roads & Perimeter | Service roads | Service/perimeter road surface and expansion joints repaired; signage; vehicle control markings. | Evidence + Site Physical Verification | Asset | examine | Road surface, joints, signage and markings are all read on the road. | Drive or walk the service/perimeter roads checking pavement condition, expansion joint condition, signage presence/legibility and vehicle control markings; specifically check whether the locations flagged in the March 2025 finding have actually been repaired. | Road pavement and expansion joints sound, signage present and legible, vehicle control markings visible — and the specific locations from the March 2025 finding actually repaired. | evidence stub: "Site inspection; work orders" bundles pavement condition, signage and markings — the same three the runway gets as separate checks
KSIA-CIV-056 | Civil | Perimeter / Security Fence | Integrity | Security fence integrity, clear zones, patrol/inspection records, gates and access control functional. | Evidence + Site Physical Verification + Question | Asset | examine | A hole in a fence is seen. The patrol records bundled in are a separate, document-shaped question. | Walk or drive a representative length of the perimeter fence checking for holes, gaps, sagging or corroded sections, or anything that could be climbed; check the clear zone for vegetation or stored materials blocking sightlines; test or observe a sample gate/access-control point in use. | Perimeter fence with no holes, gaps, sagging or corroded sections and nothing climbable against it; clear zone free of vegetation and stored materials, perimeter grass under 20 cm across the 3 m band; weekly gate visual checks and monthly condition monitoring records; fence voltage tests within the site design range; and a sample gate and access-control point observed working. | evidence stub: 'Inspection records' bundles fence condition (Asset), clear zones (Asset), patrol records (Document) and gate/access-control function (Asset) | split the patrol and inspection record half out as a Document check — weekly gate checks, monthly condition monitoring, fence voltage tests against the design range
KSIA-BFM-001 | Building & Facilities | Certificates | Certificates | Certificates in Respect of Building | Evidence + Site Physical Verification | Document | reconcile | A per-building certificate register; the walk compares current use and layout to what the register says the building is. | Walk the building and compare its current use and floor layout (tenants, subdivisions, extensions) against what the certificate register says it should be; flag any mismatch that would require a fresh certificate. | A single file/register per building listing all certificates held for it: Certificate of Occupancy, electrical CoC, fire installation Form 4/compliance certificate, structural Form 4; the building's current use and floor layout noted alongside the register.
KSIA-BFM-002 | Building & Facilities | Certificates | Certificates | Occupancy Certificate | Evidence + Site Physical Verification | Document | reconcile | The original Certificate of Occupancy and any plan-approval for changes; the walk finds retail units or extensions the CoC does not cover. | Walk the building's floor layout and compare current use/tenanting (e.g. retail units added in circulation areas, a new pier or extension) against the use and layout described on the Certificate of Occupancy. | The building's original Certificate of Occupancy (erf number, building description, approved use); proof (a further CoC or plan-approval record) for any subsequent alteration, extension or change of use.
KSIA-BFM-003 | Building & Facilities | Certificates | Certificates | Certificates of Competence- Electrical | Evidence + Site Physical Verification | Document | examine | Current electrical CoC from a registered person; the walk looks for a new DB or tenant fit-out wiring not covered by a supplementary CoC. | Inspect the distribution board(s)/installation for any visible addition or alteration (new DB, tenant fit-out wiring) and check it is covered by a supplementary CoC on file; note the registered person's details on the CoC for verification. | Current electrical CoC for the building/installation, issued by a registered person; the underlying test report; any supplementary CoC(s) for additions/alterations made since the original.
KSIA-BFM-004 | Building & Facilities | Certificates | Certificates | Certificates of Competence- Fire | Evidence + Site Physical Verification | Document | reconcile | Form 4 plus a fire compliance certificate within 12 months; the walk reads extinguisher, sprinkler and emergency-lighting tags for current dates. | 2. Physically check extinguisher service tags for current-year dates, sprinkler/hydrant service tags, and emergency lighting discharge-test labels on a sample of units; check the monthly visual-inspection log book is kept and matches what is found on the units. | 1. Original SANS 10400-A Form 4 fire-system completion certificate. 2. Current (within 12 months) fire compliance certificate; extinguisher service tags; fire detection/alarm annual test certificate; sprinkler annual flow-test certificate; emergency lighting discharge-test certificate.
KSIA-BFM-005 | Building & Facilities | Certificates | Certificates | Certificates of Competence- Structural System | Evidence + Site Physical Verification | Document | examine | Form 4 for the structural system with the engineer's ECSA registration; the walk finds visible alterations lacking updated certification. | Where structural alterations are visible on site (added floors, altered load paths, new structural elements), check whether an updated Form 4/engineer's certification exists for that altered portion. | SANS 10400-A Form 4 (Certificate of Completion of the Structural System); evidence of the appointed engineer's ECSA registration at the time of appointment.
KSIA-BFM-006 | Building & Facilities | Certificates | Statutory certificates | Occupancy certificates, local-authority fire compliance, electrical CoC per building and lift/escalator certificates available and current. | Evidence + Site Physical Verification | Document | reconcile | Occupancy, fire, electrical and lift certificates current. | 1. Compare the building's current use/layout on the ground against what the certificate describes. 2. Check fire safety equipment (extinguishers, alarms) for current service tags. 3. Check distribution boards for any un-certified additions/alterations. 4. Check each lift/escalator for its certificate/inspection plate showing a current, unexpired date. | An occupancy certificate describing the building's CURRENT use and layout, local-authority fire compliance current, an electrical Certificate of Compliance per building in the latest SANS 10142-1 format with its test report and not older than two years, and current lift/escalator certificates — all accounted for in the yearly COC reconciliation across the BDG, SBD, TRF and LGT asset groups. | evidence stub: 'Certificate file' | four certificate families with four different issuers and intervals in one row
KSIA-BFM-007 | Building & Facilities | Concrete Structures | Concrete Structures | Assess Surface Condition of Concrete (Corrosion, Cracking, Delamination, Scaling, Spalling, Popouts, Exposed Reinforcement, etc) | Evidence + Site Physical Verification | Asset | examine | Corrosion, cracking, delamination, spalling, exposed reinforcement. The survey report records the condition; the concrete IS the condition. | Walk accessible concrete surfaces (columns, soffits, beams, slabs) for corrosion staining, cracking, delamination (sounding/tap-test where feasible), scaling, spalling, popouts and exposed reinforcement, and compare against the findings/ratings in the latest survey. | Most recent structural condition/visual survey report, prepared by a registered engineer or competent inspector, rating each defect type; ACSA's internal procedure setting the required inspection interval.
KSIA-BFM-008 | Building & Facilities | Concrete Structures | Concrete Structures | Assess Distress Indicators(Cracking, Staining, Leaking, etc) | Evidence + Site Physical Verification | Asset | examine | Visible cracking, staining, leaking on structure and facades. | Look for visible cracking, staining or leaking on structural elements and facades, and check whether any such observation is already logged in the inspection report or has an open remedial job card linked to it. | Distress-indicator findings section of the structural inspection report (cracking, staining, leaking); where flagged as potentially unsafe, evidence of notification to the local authority/ACSA engineering and of remedial action taken.
KSIA-BFM-009 | Building & Facilities | Concrete Structures | Concrete Structures | Assess Alignment of Structure (Settlement, Deflection, Expansion, Contraction, etc) | Evidence + Site Physical Verification | Asset | examine | Settlement and deflection, read off crack-width monitors and level-survey points at the structure. | Check any installed movement-monitoring devices (crack-width monitors, level-survey points) are being read/recorded on schedule, and visually inspect known movement joints/cracks for width or progression against the last recorded reading. | Survey or monitoring records (visual or instrumented — crack-width monitors, level surveys) assessing settlement, deflection, expansion/contraction against the structure's design serviceability limits, with engineer's sign-off.
KSIA-BFM-010 | Building & Facilities | Roofs & Waterproofing | Condition | Roof sheeting, gutters, downpipes and waterproofing intact; no leaks/ponding; ceiling water damage repaired. | Evidence + Site Physical Verification | Asset | examine | Ponding, loose sheeting, blocked downpipes, failed waterproofing. | Walk accessible roof areas for standing water (ponding), damaged/loose sheeting, blocked or damaged gutters and downpipes, and failed waterproofing (bubbling, cracking, lifted membrane); check ceilings inside for water staining indicating an active or recent leak. | Roof sheeting sound and fixed, gutters, drop boxes and downpipes clear and undamaged, waterproofing intact with no bubbling, cracking or lifted membrane, no ponding on the roof, and no ceiling water damage left unrepaired — against three-monthly roof/gutter/drop box inspections and monthly ceiling, walkway and canopy inspections, with a work order raised for each defect. | evidence stub: 'Inspection; work orders'
KSIA-BFM-011 | Building & Facilities | Building Drainage | Building Drainage | Owner of the site shall provide drainage installation for disposal of water-borne Sewage | Evidence + Site Physical Verification | Document | reconcile | Approved drainage plans and confirmation of the municipal connection or approved on-site system; the walk traces the connection point to the plan. | Trace the visible sewer connection point/manhole (or on-site system — conservancy/septic tank, French drain) and confirm it matches the approved drainage plan; where an on-site system is used, check it is being serviced/pumped and appears adequate for current occupancy. | Approved drainage/sewer connection plans; confirmation of municipal sewer connection or, where none exists, documentation of the approved on-site system; related completion/test records.
KSIA-BFM-012 | Building & Facilities | Building Drainage | Building Drainage | Check Availability of design documents | Evidence + Question | Document | none | Approved drawings, design reports and O&M manuals, with where they are version-controlled. | — nothing to inspect on site | Approved drawings; structural/rational design reports; O&M manuals; confirmation of where and how they are stored/version-controlled (e.g. ACSA document management system or CMMS attachment), reflecting as-built/later alteration work. | the row's own question asks whether they are accessible to the SITE team or only at head office — that is a different test from whether they exist
KSIA-BFM-013 | Building & Facilities | Building Drainage | Building Drainage | Check controls for " Objectionable Discharge" | Evidence + Site Physical Verification | Asset | examine | Traps and vents correctly installed and in condition, and odour at the outlets. Odour is not a documentary fact. | Inspect accessible traps and vents for correct installation and condition, and note any odour at drainage outlets or discharge points; cross-check against the maintenance log for related complaints. | Records showing the drainage installation's trap/vent configuration matches approved design (as-built drawings); any record of nuisance/odour/pollution complaints or incidents and their resolution.
KSIA-BFM-014 | Building & Facilities | Building Drainage | Building Drainage | Check Records for Odour Control | Evidence + Site Physical Verification | Document | examine | Scheduled-versus-actual servicing dates for grease traps, vent stacks and sumps; the walk looks for buildup and overflow staining that contradict the log. | Check grease traps, vent stacks and sump pump-out points for odour and signs of overdue servicing (buildup, overflow staining), and compare against the servicing log dates. | Servicing/pump-out records for odour-generating components — grease traps, vent stacks, sump pump-outs — showing scheduled versus actual servicing dates.
KSIA-BFM-015 | Building & Facilities | Building Drainage | Building Drainage | Records for inspection of "Industrial Effluent" installations | Evidence + Site Physical Verification | Document | examine | Trade-effluent discharge consent and meter/desludging logs; the walk confirms the meters and sumps are present and functional. | Physically inspect flow meters, filtration sumps and holding sumps for effluent-generating operations (workshops, de-icing, vehicle wash bays) to confirm they are present, working, and recently desludged/read, matching the logged records. | Trade-effluent discharge consent/permit from the local water services authority; meter-reading logs; sump inspection/desludging records; periodic effluent sample test results, checked against the permit's discharge limits.
KSIA-BFM-016 | Building & Facilities | Building Drainage | Building Drainage | Records of installation tests ( PP26 or PP27) | Evidence | Document | none | Drain test certificates dated and signed off before the pipework was covered. Nothing is visible now — that is the point of the record. | — nothing to inspect on site | 1. Test certificate/record showing the drain test (PP26/clause 4.26) result, dated and signed off before the pipework was covered. 2. Test certificate/record showing the discharge/ventilating pipe test (PP27/clause 4.27) result, dated and signed off before the pipework was covered.
KSIA-BFM-017 | Building & Facilities | Building Drainage | Building Drainage | Records of Maintenace Inspections & Job cards | Evidence + Site Physical Verification | Practice | examine | Tests whether a job card marked completed means the work was done. Sample a closed card and look for the repaired item on site. | Select a sample of recently "completed" job cards and check on site whether the described work is actually evident (repaired item, replaced part); check whether any open job cards for visible defects remain unresolved. | CMMS job-card history for the asset for the last 12 months, showing scheduled versus completed maintenance inspections; ACSA's internal maintenance procedure defining required frequency/format. | evidence stub
KSIA-BFM-018 | Building & Facilities | Stormwater Disposal | Stormwater Disposal | Owner of the site shall provide suitable means for control and disposal of Stormwater … | Evidence + Site Physical Verification | Asset | examine | The requirement is that suitable means EXIST — channels, pipes, outlets present, functional and matching the plan. | Walk the site's drainage lines/outfalls and check the physical stormwater system (channels, pipes, outlets) is present, functional and matches the approved plan, noting any hardstanding/apron extensions not reflected in the plan. | Approved stormwater management plan/drawings for the site.
KSIA-BFM-019 | Building & Facilities | Stormwater Disposal | Stormwater Disposal | Check availability of stormwater components | Evidence + Site Physical Verification + Question | Asset | examine | Sight each component for damage, disconnection or infilling. | Walk down and sight each listed component (gutters, downpipes, valleys, drains, channels, retention/attenuation ponds), checking for damage, disconnection, infilling or repurposing against the as-built drawings. | As-built stormwater drawings showing gutters, downpipes, valleys, drains, channels and retention/attenuation ponds.
KSIA-BFM-020 | Building & Facilities | Stormwater Disposal | Stormwater Disposal | Records of Maintenace before rainfall season | Evidence + Site Physical Verification | Document | examine | The seasonal schedule and completed job cards; the walk finds debris that should have been cleared before the season. | Inspect stormwater channels, inlets and outlets — including less-visible ones like retention pond inlets — for vegetation/debris buildup that should have been cleared ahead of the rainy season. | ACSA's seasonal/pre-rainfall maintenance schedule; completed job cards/records showing vegetation and debris clearing was carried out ahead of the rainy season for this asset.
KSIA-BFM-021 | Building & Facilities | Stormwater Disposal | Stormwater Disposal | Clearing & Maintenance programme | Evidence + Site Physical Verification | Practice | examine | Tests whether the programme is run — accumulated silt against a schedule that says it was cleared is the finding. | Check the condition of stormwater infrastructure for evidence of recent clearing (versus accumulated silt/debris), and compare against the programme's stated schedule and the dates of recent significant rainfall events. | Written clearing and maintenance programme document; records of reactive clearing/inspection carried out after specific rainfall events in the last 12 months.
KSIA-BFM-022 | Building & Facilities | Stormwater Disposal | Stormwater Disposal | Check availability & effectiveness of Access points | Evidence + Site Physical Verification | Asset | examine | A manhole paved over or silted up cannot be inspected, whatever the drawing shows. | Locate each manhole/access chamber against the as-built drawings and check it is not paved/tarred over, is not silted up, and can be opened for inspection. | As-built drawings/manhole location plan, to verify chamber locations against site condition.
KSIA-BFM-023 | Building & Facilities | Water & Plumbing | Water & Plumbing | Maintenance of Water Infrastructure & Quality of water | Evidence + Site Physical Verification + Question | Document | examine | SANS 241 test certificates; the walk checks non-potable outlets carry legible marking. | 2. Walk the site identifying any non-potable outlets (irrigation taps, industrial-use points) and check each carries clear, legible marking distinguishing it from potable water. | 1. Most recent drinking-water quality test certificate(s) against SANS 241 limits; where ACSA operates its own borehole/reticulation, the sampling schedule/procedure. 2. Proof non-potable outlets are clearly marked. | the row's own question asks whether the supply is municipal or ACSA-operated — the sampling obligation differs completely
KSIA-BFM-024 | Building & Facilities | Water & Plumbing | Systems | Hot-water temperatures, odour control, backflow prevention, leak detection, ablution fixtures functional. | Evidence + Site Physical Verification + Question | Asset | examine | Measured outlet temperature, sewer odour in ablutions, fixtures functional. | 1. Check a sample of hot water outlets with a thermometer (or ask staff to demonstrate a recent reading). 2. Walk ablution areas and note any persistent drain/sewer odour. 3. Locate backflow prevention devices at key connection points and check for a current test tag/label. 4. Test a sample of ablution fixtures for correct operation and check for visible leaks, drips or damage. | Hot water measured at the outlet within the design range, no persistent drain or sewer odour in ablutions, backflow prevention devices fitted and tested where required, leaks found and closed out on the monthly water reticulation inspection, and ablution fixtures working — with the two-hourly signed ablution sheet countersigned and the weekly B&FM audit on file. | evidence stub: 'Inspection; maintenance records' the row's own question asks whether ACSA has a defined temperature standard at all
KSIA-BFM-025 | Building & Facilities | Refuse Disposal | Refuse Disposal | Any building shall be provided with storage area for refuse containers | Evidence + Site Physical Verification | Asset | examine | Impervious surfaces, vermin protection present and intact. | Locate the refuse storage area on site and check its surfaces are impervious and easily cleaned, weather/vermin protection (covers, screening) is present and intact, and its size matches current refuse generation. | Approved building plans showing the designated refuse storage area.
KSIA-BFM-026 | Building & Facilities | Refuse Disposal | Refuse Disposal | Check Availability of storage area | Site Physical Verification | Asset | examine | Sight the area against the drawings, and look for informal collection points that are not on any drawing. | Sight the refuse storage area directly against the approved drawings during the site walk-down, and check for any informal/unofficial additional refuse collection points that have grown up around the building. | A refuse storage area that exists on the ground where the approved drawings show it, listed in the Register of On-Site Waste Stores EMS 111, with AEMR written approval for any temporary or stakeholder-controlled area, and NO informal collection point that has grown up outside the register. NOTE: ACSA prescribes no area, volume or number — the compliance test is registration and approval, not size. | NO evidence stated
KSIA-BFM-027 | Building & Facilities | Refuse Disposal | Refuse Disposal | Check Odour control at the storage area | Evidence + Site Physical Verification | Asset | examine | Bins sealed, odour on approach, active pest control visible. | Check bins/containers at the storage area are sealed/covered, note any odour on approach, and look for evidence of an active pest-control programme (bait stations, service stickers). | Records of pest-control measures at the refuse storage area; records of bin-sealing/servicing; any log of odour-related complaints and their resolution.
KSIA-BFM-028 | Building & Facilities | Refuse Disposal | Refuse Disposal | Check frequency of waste removal | Evidence + Site Physical Verification | Document | examine | The contract or municipal schedule and three months of waybills; overflowing bins on the walk contradict them. | Check the current fill-level of refuse storage containers against the stated collection schedule (overflowing bins indicate missed/delayed collections), and look for ad-hoc overflow storage suggesting a capacity/frequency mismatch. | Refuse-removal contract or municipal collection schedule stating the contracted/required frequency; collection log/waybills for the last 3 months.
KSIA-BFM-029 | Building & Facilities | Refuse Disposal | Refuse Disposal | Check access to the strorage area | Evidence + Site Physical Verification | Asset | examine | The collection route unobstructed and not running through passenger or food-service areas. | Walk the collection-vehicle access route from the public road to the refuse storage area, checking it is unobstructed and does not pass through passenger or food-service areas; check the access gate/door can be opened by collection personnel on schedule. | Site access drawings showing the designated collection-vehicle route to the refuse storage area.
KSIA-BFM-030 | Building & Facilities | Refuse Disposal | Waste management | Waste areas hygienic, licensed removal contractors, recycling/general waste records, pest control. | Evidence + Site Physical Verification + Question | Asset | examine | Cleanliness, spillage, overflow, and recycling separation infrastructure actually in use. | 1. Visually inspect waste areas for cleanliness, spillage, overflow and hygiene. 3. Check for visible recycling separation infrastructure (labelled bins/skips) actually in use, not just present. 4. Check for pest control stations/bait boxes at waste areas and signs of vermin activity. | Waste areas clean, with no spillage or overflow; labelled recycling and general bins actually in use, not merely present; a Waste Register EMS 112 whose generated, disposed and recycled quantities reconcile; a manifest and safe disposal certificate for every removal, from a contractor whose receiving site permit is on file; and pest control records. All retained five years. | evidence stub: 'Waste manifests; contracts' | hygiene (Asset), contractor licensing (Document) and pest control in one row
KSIA-BFM-031 | Building & Facilities | Corrosion | Structural steel | Structural steel, canopies, cladding and PLB gantries, corrosion protection intact; repainting programme. | Evidence + Site Physical Verification + Question | Asset | examine | Rust staining, coating breakdown, bare steel on canopies, cladding and PLB gantries. | Inspect exposed structural steel, canopy soffits, cladding supports and PLB gantries for rust staining, coating breakdown, or bare/corroding steel, comparing observed condition against the March 2025 baseline where possible. | Structural steel, canopy soffits, cladding supports and PLB gantries with corrosion protection intact — no rust staining, coating breakdown or bare steel — against three-monthly roof and gutter rust checks and monthly canopy, walkway and paint checks, with a repainting programme whose frequency is justified by the inspection reports, and the March 2025 finding locations actually repaired. | evidence stub: 'Inspection; programme'
KSIA-BFM-032 | Building & Facilities | Movement Joints | Condition | Movement/expansion joint sealants and covers intact in terminal, walkways and parkades. | Evidence + Site Physical Verification | Asset | examine | Torn or missing sealant, damaged cover plates. | Walk terminal floors, walkways and parkade decks/ramps and inspect movement joints for torn, perished or missing sealant, damaged or missing cover plates, and any signs of water ingress or trip hazard. | Movement and expansion joint sealants intact — not torn, perished or missing — cover plates present and secure, with no water ingress or trip hazard, across terminal floors, walkways and parkade decks and ramps. Three-monthly wall expansion observations and the yearly PLB fixed-tunnel expansion joint check on record. NOTE: ACSA states no sealant type or joint gap tolerance. | evidence stub: 'Inspection'
KSIA-BFM-033 | Building & Facilities | Façades & Glazing | Safety | Curtain wall/glazing safety glass, seals, fixings; façade inspection programme. | Evidence + Site Physical Verification | Asset | examine | Cracked or chipped panels, perished seals, loose fixings. | Visually inspect accessible curtain wall/glazing panels for cracks, chips, or damage, check seals for perishing or gaps, and check fixings/brackets for looseness or corrosion, particularly at height-accessible or previously flagged locations. | Curtain wall and glazing panels uncracked and unchipped and of safety glass where required, seals unperished and gap-free, fixings and brackets tight and uncorroded — checked monthly and three-monthly — plus a façade inspection programme, and any cleaning above 1.7 m done by a certified height contractor with an approved Safety File and FALE proof of training at height. | evidence stub: "Inspection reports"
KSIA-BFM-034 | Building & Facilities | Terminal Finishes | Condition | Floors, ceilings, doors, finishes and furniture in safe condition; slip resistance; housekeeping. | Evidence + Site Physical Verification | Asset | examine | Floor damage and slipperiness near entrances and wet areas, damaged ceilings, housekeeping. | Walk terminal public and back-of-house areas checking floors for damage, wear or slipperiness (especially near entrances and wet areas), ceilings for damaged/missing tiles or water staining, doors for correct function, and general finishes/furniture for condition and housekeeping standard. | Floors undamaged and slip-resistant, especially at entrances and wet areas; ceilings without missing tiles or water staining; doors, finishes and furniture safe; housekeeping to the QMS 85% monthly cleanliness benchmark and FALE's ASQ rating of 4.2, with helpdesk logs evidencing the 5-minute response and 15-minute correction the FALE SLA requires. | evidence stub: "Site inspection"
KSIA-BFM-035 | Building & Facilities | Accessibility & Signage | Compliance | Universal access (ramps, lifts, ablutions), way-finding and statutory safety signage. | Evidence + Site Physical Verification | Asset | examine | Ramp gradients, accessible lifts in service, accessible ablutions unlocked and not used for storage. | 1. Check ramp gradients are reasonable and unobstructed, accessible lifts are in service, and accessible ablution facilities are unlocked, functional and not used for storage. 2. Walk key routes checking safety signage (exit signs, hazard warnings) is present, undamaged, correctly illuminated where required, and SANS 1186-compliant in form; check way-finding signage is clear and consistent. | Ramps at a usable gradient and unobstructed, accessible lifts in service, accessible ablutions unlocked, working and not used for storage, the disabled lift alarm button at 900-1200 mm; way-finding legible and consistent with the Wayfinding Signage Design Manual; and statutory safety signage plus exit indication present and lit, with escape routes checked clear daily. | evidence stub: 'Site inspection'
KSIA-BFM-036 | Building & Facilities | Building Maintenance | Building Maintenance | Daily Maintenance Inspection Records | Evidence + Site Physical Verification | Practice | examine | Tests whether the daily checklist is really completed daily and whether its entries match what is on the ground. | Ask to see the current daily checklist log on site (not only in a central system) and spot-check a few recent entries against actual conditions observed, to confirm they reflect real checks rather than generic sign-offs. | Daily building-condition/inspection checklist log for the asset for a representative recent period (e.g. the last month), showing it is being completed daily without gaps.
KSIA-BFM-037 | Building & Facilities | Building Maintenance | Building Maintenance | List of Closed and Outstanding Job cards | Evidence + Site Physical Verification | Practice | examine | Tests whether 'closed' means done, and whether a long-open card has a live defect behind it. | For a sample of "closed" job cards, check whether the completed work is physically evident on site; for any long-open outstanding job card, check whether the underlying defect is still visibly present. | CMMS-generated report listing all closed and outstanding job cards for the asset over the last 12 months, including how long outstanding cards have been open.
KSIA-BFM-038 | Building & Facilities | Building Maintenance | Planned maintenance | Building maintenance plan & PM completion (CMMS); backlog managed; condition grading of buildings. | Evidence + Site Physical Verification + Question | Practice | examine | Tests whether claimed PM completion is real, by spot-checking assets the CMMS says were recently serviced. | Cross-check PM completion claims against physical condition — spot-check a sample of assets shown as recently "PM completed" in the CMMS to confirm the work is evident, and look for visible signs of deferred maintenance inconsistent with a high reported completion rate. | A building maintenance plan in Oracle eAM with PM work orders executed within the 14-day or 7-day window, a backlog report scored against that window, condition grading against D060 026M's six hazards, and — the actual test — a sample of assets marked 'PM completed' showing the work is evident on site. | evidence stub: 'CMMS reports'
KSIA-EDM-001 | Energy & Demand Management | Energy Distribution | Energy Distribution | • Authority to distribute | Evidence | Document | none | A distribution licence/supply agreement. Nothing on site can make it compliant. | — nothing to inspect on site | Signed distribution/supply agreement with the municipality; NERSA distribution licence, registration, or exemption confirmation.
KSIA-EDM-002 | Energy & Demand Management | Energy Distribution | Authority | Authority/licence to distribute and resell electricity to tenants; distribution agreement with municipality. | Evidence + Question | Document | none | The agreement's SCOPE decides it — does it authorise reselling to tenants. The question reads the document, it does not replace it. | — nothing to inspect on site | The authority or licence to distribute and resell electricity to tenants, and the distribution agreement with the municipality, read for SCOPE — does it actually authorise reselling — plus tenant lease agreements carrying the energy efficiency requirements and a metering schedule showing every kiosk ready board and distribution board on the electronic metering system. | evidence stub: 'Licence / agreement'
KSIA-EDM-003 | Energy & Demand Management | Metering | Metering | 5 Yearly Calibration (>10 MVA) | Evidence + Site Physical Verification | Document | reconcile | Calibration certificate within 5 years is the pass/fail. The walk reads the meter's tag and seal to prove the certificate is THIS meter's. | Locate the >10 MVA bulk meter(s) on site, check the calibration/test tag date against the register, and check meter seals are intact. | Meter register showing capacity class and last/next calibration date for each >10 MVA metering point; calibration certificates dated within the last 5 years.
KSIA-EDM-004 | Energy & Demand Management | Metering | Metering | 10 Yearly Calibration (1 MVA - 10 MVA) | Evidence + Site Physical Verification | Document | reconcile | As 003, 10-year interval. | Locate a sample of meters in the 1–10 MVA range, check the calibration/test tag date against the register, and check seals are intact. | Meter register showing capacity class and last/next calibration date for 1–10 MVA metering points; calibration certificates dated within the last 10 years.
KSIA-EDM-005 | Energy & Demand Management | Metering | Metering | 20 Yearly Calibration (<100 kVA) | Evidence + Site Physical Verification | Document | reconcile | As 003, 20-year interval. | Spot-check a sample of small tenant/back-of-house meters for a calibration/installation date tag against the register. | Meter register showing capacity class and last/next calibration date for <100 kVA metering points; calibration certificates or installation records dated within the last 20 years.
KSIA-EDM-006 | Energy & Demand Management | Metering | Calibration | Bulk and tenant metering calibrated per NRS 057 intervals; meter register maintained; CT/VT ratios verified. | Evidence + Site Physical Verification | Document | reconcile | NRS 057 intervals evidenced by certificates and the register; the walk matches tags and CT/VT nameplate ratios to what is recorded. | 1. Check calibration tags on a sample of bulk/tenant meters against the register. 3. Check CT/VT nameplate ratios match what is recorded/programmed for that meter. | Calibration certificates for every bulk and tenant meter held by the Electrical Maintenance Department, calibration tags on the meters matching the register, CT/VT nameplate ratios matching what is recorded and programmed for that meter, and a transformer routine test report evidencing the CT ratio and polarity check. NOTE: ACSA states no calibration interval — NRS 057 supplies it. | evidence stub: 'Calibration certificates; register'
KSIA-EDM-007 | Energy & Demand Management | Tariffs & Billing | Tariff verification | Municipal tariff category verified as correct; supplies reconciled against bills; no unbilled premium supplies (kick-off risk item 6.5.1). | Evidence + Site Physical Verification + Question | Practice | reconcile | Tests whether reconciliation actually CATCHES everything — an unbilled supply is found by walking the site, not by reading the reconciliation that omits it. | Confirm every metering point/intake substation on site is accounted for in the reconciliation list — look for a supply (e.g. newer building, generator, tenant connection) without a corresponding municipal account. | A reconciliation of every metering point and intake substation on site against the municipal bills, with the tariff category confirmed correct for the demand profile, and NO supply found on the walk — a newer building, a generator, a tenant connection — that has no corresponding municipal account. This is kick-off risk item 6.5.1 and an unbilled premium supply is found by walking, not by reading the reconciliation that omits it. | evidence stub: 'Bills vs meter data reconciliation'
KSIA-EDM-008 | Energy & Demand Management | Energy Consumption | Energy Consumption | • Energy Optimisation | Evidence + Site Physical Verification | Document | examine | The kWh figures and % change are the proof; the walk confirms the claimed initiatives physically exist and run. | Confirm cited optimisation initiatives (e.g. LED retrofits, VSDs, control upgrades) are physically installed and operating as claimed. | Prior FY actual kWh; current FY actual (or annualised) kWh; the % change calculation; register of optimisation initiatives implemented and their estimated savings.
KSIA-EDM-009 | Energy & Demand Management | Energy Consumption | Energy Consumption | • Cost Savings | Evidence + Question | Document | none | A documented target and the actual Rand saving with its calculation basis. | — nothing to inspect on site | Any documented cost-saving target and actual Rand savings achieved, with the calculation basis (e.g. avoided cost vs. baseline tariff x baseline consumption).
KSIA-EDM-010 | Energy & Demand Management | Energy Consumption | Energy Consumption | • Emmision Reduction | Evidence | Document | none | Prior and current figures with the methodology. | — nothing to inspect on site | Prior and current FY kWh (and/or calculated tCO2e) figures with the % change calculation; emissions calculation methodology used.
KSIA-EDM-011 | Energy & Demand Management | Energy Consumption | Monitoring | Monthly consumption records; KPIs (kWh/pax, kWh/m²) tracked against targets; energy saving initiatives tracked. | Evidence + Site Physical Verification | Document | reconcile | Monthly records and KPIs against targets; the walk confirms the dashboards those reports cite are live. | Spot-check that BMS/metering dashboards referenced in the reports are live and showing current data. | Monthly consumption records for KSIA with kWh/pax and kWh/m² tracked against a stated target, hourly energy-use model data per asset, system, process or area, BMS out-of-range alerts raised as CMMS energy audit job cards, and the dashboards the reports cite live and showing current data on the walk. | evidence stub: 'Energy reports'
KSIA-EDM-012 | Energy & Demand Management | NMD | NMD | Ensure that max demand never exceed NMD. When an airport exceed their NMD more than once in a given month, a penalty is levied over the next 12 months | Evidence | Document | none | Interval demand data against the registered NMD, plus any penalty notices. | — nothing to inspect on site | Demand profile/interval data (e.g. 30-minute kVA readings) from the bulk supply meter for the review period; the registered NMD value; any penalty notices/invoices.
KSIA-EDM-013 | Energy & Demand Management | NMD | Demand management | Maximum demand never exceeds Notified Maximum Demand; NMD penalties tracked; load-shedding/peak strategy. | Evidence + Site Physical Verification | Practice | examine | Tests whether the peak/load-shed strategy is real — equipment configured AND control-room staff able to say how a peak is managed. | Confirm demand-management equipment (e.g. BMS demand-limiting function, generator/load-shed triggers) is physically installed and configured; ask control-room/BMS staff how an approaching demand peak is identified and managed. | Interval demand data showing maximum demand never exceeding the registered Notified Maximum Demand, municipal accounts checked for exceedance penalties, and a peak/load-shed strategy that physically exists — demand-limiting configured in the BMS, generator or load-shed triggers installed — with control-room staff able to describe what happens as a peak approaches. NOTE: ACSA states no NMD figure or penalty rule. | evidence stub: 'Demand profile data' | NMD compliance (a figure) and demand-management practice are two different tests in one row
KSIA-EDM-014 | Energy & Demand Management | Solar PV Plant | Solar PV Plant | Annual maintenance, ensuring optimal performance and preservation of warranties and guarantees | Evidence + Site Physical Verification | Document | examine | Service report within 12 months is the pass/fail; the walk checks service tag, cleanliness, damage, fault indicators. | Inspect the PV array and inverter enclosure for a current service tag/sticker, visible cleanliness, and no obvious loose cabling, damaged panels, or unresolved fault indicators. | Annual PV maintenance service report/certificate dated within the last 12 months; O&M manual/warranty terms specifying the required maintenance; CoC reissued or confirmed after maintenance per D060 004, where applicable.
KSIA-EDM-015 | Energy & Demand Management | Solar PV Plant | Solar PV Plant | Min Irradiance Threshold (MIT) (all ACSA plants are designed at 50-70 W/m2) | Evidence + Site Physical Verification | Document | examine | SCADA irradiance-vs-output data is the proof; the walk checks the pyranometer is clean and correctly positioned, because a dirty sensor invalidates the data. | Check the on-site irradiance sensor/pyranometer is clean, undamaged and correctly positioned (a dirty/obstructed sensor gives false readings), and confirm the monitoring dashboard is live with current data. | PV monitoring/SCADA data showing irradiance vs. generation output, with any low-irradiance startup failures flagged.
KSIA-EDM-016 | Energy & Demand Management | Solar PV Plant | Solar PV Plant | Performance Ratio and Plant efficiency | Evidence + Site Physical Verification + Question | Document | examine | PR reports monthly and rolling annual; the walk looks for soiling, shading and damaged panels that explain a low PR. | Inspect the array for visible soiling, shading obstructions, or damaged/discoloured panels, and check inverters for fault codes or reduced-output warnings. | PV monitoring system PR reports (monthly and rolling annual).
KSIA-EDM-017 | Energy & Demand Management | Solar PV Plant | Solar PV Plant | Array is not shaded | Site Physical Verification + Question | Asset | examine | THE CLEANEST ASSET CASE HERE. Shadow on panels. No document can establish it — you stand there and look, at the right time of day. | Visually check for shadow falling on panels from trees, structures, or equipment at the time of the site visit — especially early morning/late afternoon when shadows are longest; check string-level monitoring, if available, for consistent underperformance on particular rows. | No shadow falling on any panel from trees, structures or equipment at the time of the visit — checked early morning or late afternoon when shadows are longest — and string-level monitoring showing no string persistently underperforming its neighbours, which is shading the eye missed. | NO evidence stated at all
KSIA-EDM-018 | Energy & Demand Management | Solar PV Plant | Performance & maintenance | PV performance ratio monitored; inverter and panel maintenance/cleaning records; PV installation CoC; earthing/lightning protection. | Evidence + Site Physical Verification | Document | examine | CoC and maintenance/cleaning records; the walk checks soiling, inverter ventilation clearance and cable labelling. | 1. Confirm the PV monitoring system is live on site. 2. Check panels for soiling and inverters for cleanliness, ventilation clearance, and absence of fault indicators. 3. Spot-check DC/AC combiner box and cable labelling for consistency with the CoC. 4. Visually inspect earthing conductors, bonding, and surge protection devices at the array/inverter for physical integrity (no corrosion, disconnection, or damage). | Performance ratio monitored on a live system, inverter and panel cleaning and maintenance records, a PV installation Certificate of Compliance in the latest SANS 10142-1 format with its test report and not older than two years, and earthing and lightning protection test results. NOTE: the earthing results are not required by any ACSA clause found — they must be requested. | evidence stub: 'Monitoring data; CoC' | PR monitoring, maintenance records, CoC and earthing/lightning protection are four tests in one row
KSIA-EDM-019 | Energy & Demand Management | Energy Storage | Energy Storage | • Grid Connection - agreement with utility to export • Land rights - submission to the council • Environmental - depending on technology. Hydro one must comply with regulations under water section and battery storage must comply with • Wheeling agreements | Evidence + Question | Document | none | Four separate approvals — grid connection, land rights, environmental, wheeling. The question establishes which apply, not whether they exist. | — nothing to inspect on site | 1. Signed grid connection/export agreement; grid code compliance confirmation. 2. Land rights submission and council approval. 3. Environmental authorisation matching the storage technology (e.g. water use licence). 4. Signed wheeling agreement. |  | four approval types, four different authorities
KSIA-EDM-020 | Energy & Demand Management | Energy Storage | Safety | Battery storage: ventilation, fire detection/suppression, isolation, manufacturer maintenance. | Evidence + Site Physical Verification | Asset | examine | Ventilation unobstructed, detector heads present and undamaged, isolation switches labelled and accessible. The battery room's state decides. | 1. Check ventilation louvres/fans are unobstructed and, where mechanical, running. 2. Check detector heads are present and undamaged, with current service tags. 3. Locate isolation switches and confirm labelling and accessibility. 4. Check current service tags and any visible damage, corrosion, or thermal distress on battery cabinets. | Ventilation louvres and fans unobstructed and running, fire detection heads present, undamaged and in service tag date, gas suppression maintained yearly with cylinders inside the 10-yearly hydrostatic test, isolation switches located and labelled, manufacturer maintenance current, and the room inside 0-40 °C and 20-80% RH. NOTE: D118MAN cl. 8.6 requires lithium-ion for UPS batteries. | evidence stub: 'Inspection'
KSIA-EDM-021 | Energy & Demand Management | BMS & Controls | Optimisation | BMS set-points and schedules optimised; alarms managed; plant not in manual override. | Evidence + Site Physical Verification | Practice | examine | Plant left in manual override and aged unresolved alarms are a practice failure, not a document failure. The BMS screen is where you see it. | In the BMS control room, check for any plant left in 'manual/hand override' and check the active alarm list for unresolved/aged alarms; cross-check a sample of plant on site is running per its scheduled state. | No plant left in manual or hand override, the active alarm list free of unresolved or aged alarms, set-points and schedules matching what the plant is actually doing on site, car park lighting at 100% on presence and 40% on absence, motion sensor timeouts configured as specified, and BMS out-of-range alerts converted to CMMS energy audit job cards. | evidence stub: 'BMS screenshots/logs'
KSIA-EDM-022 | Energy & Demand Management | Green Buildings | Green Buildings | Green Star Ratings certification | Evidence | Document | none | Green Star certificate with rating level and validity. | — nothing to inspect on site | Green Star certificate(s) for the applicable building(s), showing rating level and validity/expiry; SANS 204 compliance documentation.
KSIA-EDM-023 | Energy & Demand Management | Water | Water | Any tariff set by a water services institution for the supply of water services to a consumer to have an agreement in place with the relevant tariff | Evidence | Document | none | Water supply agreement, tariff schedule, invoices matching the agreed tariff. | — nothing to inspect on site | Signed water supply agreement(s) with the relevant water services institution; the current tariff schedule; recent water invoices matching the agreed tariff.
KSIA-EDM-024 | Energy & Demand Management | Water | Water management | Water metering, consumption KPIs, leak detection programme, rain/grey-water use. | Evidence + Site Physical Verification | Practice | examine | Tests whether a leak-detection programme is actually run — walking pipework for damp patches and pooling is how you find out. | 1. Locate bulk and key sub-meters and confirm they are functional and readable. 3. Walk visible pipework and known problem areas for signs of leakage (damp patches, pooling, unusually lush vegetation). 4. Inspect any rainwater/grey-water infrastructure for signs it is connected and in use, not disused or bypassed. | Bulk and sub-meters functional and readable, monthly or quarterly consumption recorded, a continual leak investigation programme with walkabout records for leaking tanks and pipelines, monthly water reticulation inspections covering meter operation, rain and grey-water use where installed, and the Register of Effluent and Storm Water Discharge Points EMS 105 current. | evidence stub: 'Water reports'
KSIA-EDM-025 | Energy & Demand Management | Emissions | Emissions | •measurement of hydrocarbons (HC), carbon monoxide (CO), carbon dioxide (Co2) and oxides of nitrogen (NOx) to determine mass emissions through calculations during aircraft landing and take-off cycle (LTO). to comply with ICAO 9889 & Annex 16 • The LTO cycle is based on times in mode data during high activity periods at major airports for four modes of engine operation: taxi/idle, take-off, climb-out and approach. • The mass emissions for these modes are combined to yield the reported emissions certification levels. • ICAO 9889 section 2.4.4 refers to LTO of 915 m | Evidence + Site Physical Verification + Question | Document | examine | The LTO emissions inventory against ICAO 9889 methodology; the walk confirms the ambient monitoring station that feeds it is installed, calibrated and running. | Confirm any on-site ambient air quality monitoring station is installed, calibrated, and operating, since its data feeds emissions/air-quality reporting. | Most recent LTO emissions inventory/calculation report showing methodology, time-in-mode data, and resulting mass emissions per pollutant; any ambient air quality monitoring data cross-referenced against SANS 1929 limits.
KSIA-EDM-026 | Energy & Demand Management | Emissions | Carbon reporting | GHG emissions calculated and reported; reduction targets tracked. | Evidence | Document | none | Emissions report with reduction targets tracked. | — nothing to inspect on site | Carbon footprint calculations for KSIA against a stated boundary and methodology, the ACI Airport Carbon Accreditation certificate, environmental objectives and targets set under the KSIA EMS with review records, and the reduction trend in the Integrated Annual Report — supported by the annual EMS peer-review audit and the ISO 14001 certification cycle. | evidence stub: 'Emissions report'
KSIA-PSR-001 | Process Safety & Risk | Hazard Identification & Risk Assessment | HIRA | Site HIRA conducted per B170 001M, reviewed annually or after change/incident; risk register maintained with controls and owners. | Evidence + Site Physical Verification | Document | examine | HIRA reviewed annually and a maintained register is the pass/fail; the walk spot-checks that listed controls physically exist as described. | Spot-check 2-3 risks from the register on site (e.g. a barrier, lockout point, signage) to confirm the listed control physically exists as described. | A site HIRA to B170 001M using the 25-cell Severity A-E × Likelihood 1-5 matrix, reviewed annually or after any change or incident, with the eight-column ICAO SMM log carrying both the initial (column 6) and residual (column 8) Safety Risk Index, controls and named owners against each risk, evidence of all five B170 cl. 4.1 triggers, HIRA reports submitted to the SACAA Director of Civil Aviation — and 2-3 listed controls confirmed to physically exist on site as described. | evidence stub: 'HIRA; risk register'
KSIA-PSR-002 | Process Safety & Risk | Hazard Identification & Risk Assessment | Management of change | Changes to plant, configuration or procedures (e.g. abnormal electrical network configurations) risk-assessed and approved before implementation. | Evidence + Question | Practice | none | Tests whether change control happens BEFORE implementation. A current abnormal configuration that never went through MOC is the failure, and only asking finds it. | — nothing to inspect on site | An Engineering Asset Modification Request M&E 088 for every change, a change record in the Asset Modification Register for every request INCLUDING rejected ones, the five sequential D060 020M stages evidenced in order (each a prerequisite of the next), the ten mandatory steps for tenant-initiated modifications, a formal HIRA before each named trigger, and Asset Modification Committee minutes approving it before implementation. | evidence stub: "MOC records"
KSIA-PSR-003 | Process Safety & Risk | Hazard Identification & Risk Assessment | Safety-critical controls | Controls for top site risks (fuel, electrical, working at heights, airside vehicles) verified in place and effective; control owners assigned. | Evidence + Site Physical Verification | Asset | examine | A control 'verified in place and effective' is settled by finding the bonding, the lockout point, the fall-arrest anchor. The register listing it proves nothing. | Physically check a sample control per risk area - e.g. fuel: overfill/bonding protection; electrical: a lockout/isolation point; heights: fall-arrest anchors/edge protection; airside vehicles: speed-control signage or escort in practice. | A control physically checked per top risk area — fuel: overfill and bonding protection; electrical: a lockout/isolation point; heights: fall-arrest anchors and edge protection; airside vehicles: speed control — each traceable to the Compliance Risk Management Plan GOV 006 with all nine mandatory fields including residual rating, responsibility and target date, and the residual band matched to the mandated strategy (Avoidance / Reduction / Segregation of exposure). | evidence stub: "Risk register; verification evidence"
KSIA-PSR-004 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | MHI compliance | Fuel farm: MHI notification & risk assessment, emergency plan, bund/containment, hydrant pit lids preventing water ingress and environmental contamination. | Evidence + Site Physical Verification + Question | Asset | examine | Cracked bund walls and water in hydrant pits fail this whatever the paperwork says. | Walk the fuel farm: check bund walls for cracks/damage and confirm the bund is dry with drain valve closed; check hydrant pit lids sit flush with no water pooling; look for MHI notification signage. | MHI notification on site with signage, an AIA risk assessment within five years, an emergency plan tested within twelve months and submitted to NERSA annually, bund walls uncracked and the bund dry with its drain valve closed, and hydrant pit lids sitting flush with no water pooling — water in a pit is both the ingress and the contamination route this check exists for. | evidence stub: 'MHI RA; emergency plan; inspection' | MHI notification and risk assessment (Document) sit in the same row as bund and pit-lid condition (Asset) — two different failures, one row
KSIA-PSR-005 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Hazardous area classification | Hazardous-area classification drawings for fuel farm, hydrant pits and generator rooms; Ex-rated equipment inspected and maintained. | Evidence + Site Physical Verification | Document | reconcile | Hazardous-area classification drawings and Ex inspection records; the walk matches Ex markings and tags on fittings to the classified zones on the drawing. | Walk the fuel farm, hydrant pits and generator rooms; confirm electrical fittings in classified zones carry visible Ex markings and current inspection tags. | Hazardous-area classification drawings covering the fuel farm, hydrant pits AND generator rooms, current for the plant as built, with electrical fittings in every classified zone carrying a visible Ex marking at or above the zone's requirement and a current inspection tag. NOTE: the register names no ACSA evidence for this check — the drawings must be requested by name. | evidence stub: "HAC drawings; Ex inspection records"
KSIA-PSR-006 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Spill response | Spill response equipment at fuelling positions and fuel farm; oil/water separators serviced; spill drills conducted; environmental incident records. | Evidence + Site Physical Verification | Asset | examine | Spill kits present, complete and in date; separator not full of oil. Presence is a physical fact. | Check spill kits at the fuel farm and fuelling positions for presence, completeness and in-date condition; check the oil/water separator for a service tag and that it is not full of oil/debris. | Spill kits at the fuel farm and at every fuelling position, sealed, complete and in date; oil/water separators with a service tag, tested annually for efficiency, sludge depth under 25% of chamber depth and not full of oil or debris; spill drills recorded; and a spillage report logged with the Helpdesk for every environmental incident, with containment inside the 2-hour limit and safe disposal certificates retained 5 years. | evidence stub: 'Inspection; drill records' | spill equipment condition, separator servicing and drill records are three tests
KSIA-PSR-007 | Process Safety & Risk | Standby Power Safety | Fuel isolation | Fire cut-out / isolation on generator diesel supply; fuel storage separation, spill containment, fire protection at generator rooms. | Evidence + Site Physical Verification + Question | Asset | examine | The fire cut-out present, labelled and accessible; the tank bunded and separated. Nothing documentary settles it. | Visit each generator room: confirm the fire cut-out/isolation point is present, labelled and accessible; check the diesel tank is separated/bunded from the generator; check fire extinguishers are present, in date and unobstructed. | A fire cut-out or isolation point in each generator room, present, labelled and accessible; the diesel tank separated from the generator and bunded to at least 110% of the largest container; fire extinguishers present, in date and unobstructed; and the weekly off-load and monthly on-load test records evidencing the fuel shut-off valve check. | evidence stub: 'Inspection'
KSIA-PSR-008 | Process Safety & Risk | Standby Power Safety | Diesel storage | Bulk diesel storage compliant: bunding, tank certification, fire separation from generator, spill containment, dispensing controls. | Evidence + Site Physical Verification + Question | Asset | examine | Bund condition, visible separation, dispensing containment. | Inspect the bulk diesel tank: bund condition (empty, no cracks, drain valve closed), certification plate, visible separation from the generator, and dispensing point containment/lock access control. | Bulk diesel tank with a certification plate, permits on file for above and underground tanks, a bund that is empty, uncracked and drain-valve-closed at at least 110% of the biggest container, visible fire separation from the generator, a contained dispensing point with access control, and the tank entered on the Register of Dangerous Goods EMS 109. | evidence stub: 'Inspection; certificates' | tank certification is a Document test inside an Asset row
KSIA-PSR-009 | Process Safety & Risk | Emergency Preparedness | Plans & drills | Aerodrome emergency plan current; evacuation & emergency drills held and recorded; emergency equipment inspected. | Evidence + Site Physical Verification | Document | examine | A current plan and recorded drills are the proof; the walk confirms the assembly points and equipment the plan NAMES are actually there and unobstructed. | Confirm emergency assembly points, signage and equipment named in the plan are actually present, visible and unobstructed on site. | A current aerodrome emergency plan, evacuation and emergency drills held and recorded within period, the Fuel Depot plan tested at least every twelve months with the practice-test records kept, Emergency Co-ordinator, Evacuation Officer and Fire Warden appointments in writing and inside their three-year validity — and the assembly points, signage and equipment the plan names actually present, visible and unobstructed on site. | evidence stub: 'Plan; drill records'
KSIA-PSR-010 | Process Safety & Risk | Emergency Preparedness | Emergency equipment | Emergency showers/eyewash, first-aid boxes, spill kits, fire equipment access and assembly points inspected and signed. | Evidence + Site Physical Verification | Asset | examine | Eyewash flows, first-aid box stocked and in date, extinguisher gauge in the green. The inspection register records it; the equipment decides it. | Sample-check emergency showers/eyewash (current tag, water flows, unobstructed), first-aid boxes (stocked, in date), spill kits (sealed/complete), fire extinguishers (in date, gauge in green, unobstructed), and confirm assembly points are marked and clear. | Emergency showers and eyewash with a current tag, water flowing and unobstructed; first-aid boxes stocked and in date at the ratio the headcount requires (one trained first aider per fifty employees, at least one per working environment, appointed on OHS 004 with a current certificate from a DoL-registered provider); spill kits sealed and complete; fire equipment in date, gauge in the green and unobstructed; assembly points signed. | evidence stub: "Inspection registers"
KSIA-PSR-011 | Process Safety & Risk | Emergency Preparedness | Lessons learnt | Incident and near-miss investigations feed the HIRA and maintenance regimes; recurring failure modes trended (e.g. generator, fuel pit). | Evidence + Site Physical Verification + Question | Practice | examine | Tests whether investigations actually feed the HIRA and whether an action marked 'closed' was really done — the walk verifies one physical corrective action. | Where a corrective action from an investigation involved a physical change (e.g. a new barrier or control), confirm on site that it was actually implemented. | Incident and near-miss investigations that visibly change something — the HIRA updated, a maintenance regime changed, a recurring failure mode (generator, fuel pit) trended — with preliminary reports inside 7 days, full reports inside one month, Annexure 1 submitted to the DoL where required, and any corrective action involving a physical change confirmed implemented on site. | evidence stub: 'Investigation reports; trend'
KSIA-PSR-012 | Process Safety & Risk | Fire Safety Management | Fire risk | Fire risk assessment current; fire compartmentation/doors, escape routes clear, fire equipment access; fire marshal appointments. | Evidence + Site Physical Verification | Asset | examine | Fire doors propped open and blocked escape routes are the failure. The FRA is context. | Walk key areas (terminal, plant rooms, fuel farm): confirm fire doors close fully and are not propped open, escape routes and fire equipment (item 4) are unobstructed, exit signage is visible/lit, and ask on-duty staff to identify the fire marshal for that area. | A current fire risk assessment; fire doors that close fully and are not propped; compartmentation intact; escape routes and fire equipment unobstructed; exit signage visible and lit with daily escape-route clearance checks; the yearly record of Fire Hazard Classes per occupancy to SANS 10400-T; council-approved designs validated yearly; and Fire Warden appointments in writing, inside their three-year validity and on the OHS Appointments Register. | evidence stub: 'FRA; inspection' | fire risk assessment and marshal appointments (Document) vs compartmentation and escape routes (Asset)
KSIA-PSR-013 | Process Safety & Risk | Fire Safety Management | Fire water & access | Fire water supply adequacy (storage, pumps, hydrant coverage) and fire-service vehicle access maintained around terminal, fuel farm and plant rooms. | Evidence + Site Physical Verification | Asset | examine | Hydrant markers visible and accessible, pump room condition, access routes not blocked by vehicles. | Confirm hydrant markers/covers are visible and accessible, the fire pump room is in good condition, and access routes to the terminal, fuel farm and plant rooms are not blocked by vehicles, materials or other obstructions. | A fire-water assessment showing storage, pump capacity and hydrant coverage adequate for the terminal, fuel farm and plant rooms; hydrant markers and covers visible and accessible; the pump room sound with its weekly and monthly test records complete and the quarterly six-hour full-load run done; and fire-service access routes clear of vehicles, materials and parked equipment. | evidence stub: 'Fire-water assessment; site walk'
KSIA-PSR-014 | Process Safety & Risk | Fire Safety Management | Hot work & permits | Permit-to-work system covers hot work, confined space, electrical isolation and working at heights; permits audited. | Evidence + Site Physical Verification | Practice | examine | A permit system exists on paper everywhere. The test is a live permit during the audit and whether the controls it lists — fire watch, gas testing, barricading — are actually in place. | If hot work, confined-space, electrical or height work is in progress during the audit, check the live permit on site and confirm the controls listed (fire watch, gas testing, barricading, fall protection) are actually applied. | A permit-to-work system covering hot work, confined space, electrical isolation and working at heights, permits signed by BOTH parties at issue AND at cancellation, gas testing results recorded on the permit face, a fire watch held at least 30 minutes after hot work with the area inspected at one hour and monitored a further three, permits audited, and any live permit on site matching the controls actually in place. | evidence stub: "Permit records (sample)"
KSIA-PSR-015 | Process Safety & Risk | Hazardous Substances & Gas | Storage & handling | Hazardous chemical inventory, SDS available, storage segregation & ventilation, LPG installations certified, confined-space & hot-work procedures. | Evidence + Site Physical Verification | Asset | examine | Flammables away from oxidisers, ventilation working, SDS physically AT the store rather than filed centrally. | Inspect the chemical storage area for segregation (e.g. flammables away from oxidisers), ventilation, SDS physically available at the store (not just filed centrally), and hazard signage; check the LPG installation for a visible CoC/compliance plate and obvious defects (corrosion, leaks, unsecured cylinders). | A hazardous chemical inventory classified to SANS 10228, SDS physically accessible at the store rather than filed centrally, storage segregated (flammables away from oxidisers), ventilated and signed, bunding at at least 110% of the biggest container, LPG installations certified, an Asbestos Register EMS 103, and confined-space and hot-work procedures approved by the GMR 2(1) and 2(7) appointees. | evidence stub: 'Inventory; SDS; CoCs' | inventory and LPG CoCs (Document) vs storage segregation and ventilation (Asset)
KSIA-PSR-016 | Process Safety & Risk | Hazardous Substances & Gas | Gas cylinders | Compressed/LPG gas cylinders stored upright, secured, segregated, ventilated, signed; empty/full separated. | Site Physical Verification | Asset | examine | Cylinders upright, chained, segregated by gas type, empty and full separated. A clean single-subject Asset check. | Physically inspect the gas cylinder storage area(s): confirm cylinders are upright, chained/strapped, segregated by gas type, area is ventilated and signed, and empty/full cylinders are clearly separated and labelled. | Cylinders upright, chained or strapped, segregated by gas type, in a ventilated and signed area, with empty and full clearly separated; Written Safe Work Procedures for compressed gas cylinders approved by the GMR 2(1) and 2(7) appointees; the Pressure Equipment Regulations register with three-yearly inspection and test; and SCBA cylinders at 300 bar and never below 80% of filling pressure, hydrostatically tested at least every 4 years. | evidence stub: 'Site inspection'
KSIA-PSR-017 | Process Safety & Risk | Statutory Appointments & Competencies | All Disciplines | GMR 2(1) Appointments | Evidence + Site Physical Verification | Document | reconcile | A signed, dated GMR 2(1) letter and competency certificate; the walk confirms the named appointee is the person actually doing it, via records bearing their name. | Confirm the named appointee is still employed and actively performing the role on site — look for inspection records, signed SOPs, and permit-to-work/lock-out records bearing their name or signature, not just the appointment letter itself. | Signed, dated GMR 2(1) appointment letter (naming the individual, premises and machinery covered) and the appointee's competency certificate/experience record.
KSIA-PSR-018 | Process Safety & Risk | Statutory Appointments & Competencies | Mechanical appointments & competencies | People Movers | Evidence + Site Physical Verification | Document | reconcile | Monthly visit records unbroken, 6-monthly rope and 12-monthly safety-gear entries present; the walk reads the unit's own on-site register. | 1. Locate the unit's on-site maintenance register and confirm monthly visit entries are unbroken and dated, and that 6-monthly rope and 12-monthly safety-gear/governor/buffer entries exist and are current. Visually check the unit runs and doors/gates interlock correctly. Pass: unbroken, dated log matching required frequencies. Fail: gaps, or generic servicing tickets in place of the prescribed checks. 2. Check the current inspection certificate's issue date is within 24 months and confirm the issuing body's accreditation, not just the maintenance contractor's own paperwork. Pass: valid, dated certificate from a confirmed accredited authority. Fail: expired, or not re-issued after a change of provider or a modification/failure event. | 1. Written appointment/contract with the lift service provider covering the specific units; monthly maintenance visit records; the 6-monthly rope-examination and 12-monthly safety-gear/governor/buffer test records. 2. The accredited inspection authority's comprehensive report/certificate, valid within the last 24 months (or re-issued after modification, failure, or change of service provider), and confirmation the authority is accredited/registered.
KSIA-PSR-019 | Process Safety & Risk | Statutory Appointments & Competencies | Mechanical appointments & competencies | Red ticket - Millwright | Evidence + Site Physical Verification | Document | reconcile | The National Artisan Certificate itself, not an attendance letter; matched to the person doing millwright work. | Match the certificate holder's name to the person actually performing millwright duties on site. Confirm the document is the actual trade test/National Artisan Certificate (not an attendance or learnership letter), and note certificate details for cross-check against the DHET National Artisan Development Support Centre trade test index where possible. Pass: genuine trade test certificate on file, name matches the person on the tools. Fail: only an attendance/learnership letter, the certificate belongs to someone else, or it's for a different trade. | The individual's original National Artisan Certificate / trade test certificate (millwright), issued via a QCTO-accredited trade test centre — not a training-attendance or learnership-completion letter.
KSIA-PSR-020 | Process Safety & Risk | Statutory Appointments & Competencies | Mechanical appointments & competencies | Fire Protection | Evidence + Site Physical Verification | Document | reconcile | Contractor SAQCC Fire registration and service records; the walk reads service tags for a legible in-interval date. | Walk the site checking service tags/labels on extinguishers, hose reels, hydrants and sprinkler heads for a legible last-service date within the expected interval (commonly annual) and next-due date. Pass: current, legible tags across devices and a valid SAQCC Fire-registered contractor. Fail: missing/expired tags or no SAQCC Fire registration on file. | ACSA's internal D080 002M procedure (request directly from ACSA); the fire-fighting maintenance contractor's appointment/contract and SAQCC Fire registration; current service certificates/tags on extinguishers, hose reels, hydrants and sprinkler heads (last-service and next-due dates).
KSIA-PSR-021 | Process Safety & Risk | Statutory Appointments & Competencies | Electrical appointments & competencies | Certificate of Compliance issuance | Evidence + Site Physical Verification | Document | reconcile | Current CoC and its test report, issuer registered; the walk checks it covers visible subsequent additions. | Locate the installation's COC and test report. Check the date against the 2-year rule where issued for a change of ownership, and confirm it covers any visible subsequent additions (e.g. a newer sub-board not matching the original COC scope). Pass: current COC/test report matching the installation as it stands. Fail: COC older than 2 years post-ownership-change, missing test report, or an uncovered addition. | Current Certificate of Compliance and its test report for each electrical installation/plant room, confirming date and the issuer's registration status.
KSIA-PSR-022 | Process Safety & Risk | Statutory Appointments & Competencies | Electrical appointments & competencies | ILS | Evidence + Site Physical Verification | Document | examine | Flight-check certificate and calibration records; the walk confirms the localizer and glide path equipment is present, powered, undamaged and free of interference. | Visually confirm the ILS ground equipment (localizer, glide path antenna, monitoring equipment) is present, powered, undamaged and free of unauthorised interference, and cross-check the equipment tag/serial against commissioning records. (Flight-check validity and the 99.8% availability figure are verified through documentation, not a physical measurement the auditor can take on site.) | Current flight-check/flight-inspection certificate (from an approved provider); ground calibration and maintenance records; availability/downtime log benchmarked against the 99.8% D109 target; technician training/competency records specific to ILS maintenance.
KSIA-PSR-023 | Process Safety & Risk | Statutory Appointments & Competencies | Electrical appointments & competencies | Trade tested and “wiremans license” | Evidence + Site Physical Verification | Document | reconcile | The trade test certificate for the electrical trade specifically, matched to the person doing the work. | 1. Match the certificate on file to the person actually carrying out electrical work on site. Confirm it is the actual trade test certificate for the electrical trade specifically. Pass: genuine certificate matching the person on site. Fail: only an attendance/learnership letter, or a certificate for a different trade. 2. Confirm the registration category matches the actual work observed (e.g. flag a Single-Phase-only registration being used on three-phase industrial work), and that the named registered person is the one actually carrying out or supervising the work. Pass: current registration matching both category and person. Fail: no separate registration on file, category mismatch, or the registered individual is not the one doing/supervising the work. | 1. The individual's original National Artisan Certificate / trade test certificate (electrical trade / "red seal") — not a training attendance or learnership-completion letter. 2. The individual's registration certificate/number (Electrical Tester for Single Phase / Installation Electrician / Master Installation Electrician) with the Department of Employment and Labour.
KSIA-PSR-024 | Process Safety & Risk | Statutory Appointments & Competencies | Electrical appointments & competencies | Aerodrome lighting and power back up systems maintenance - ICAO | Evidence + Site Physical Verification + Question | Asset | examine | Two adjacent lights out is an ICAO failure you find by driving the runway at night. The outage log records it; the runway decides it. | 1. Walk (or drive) the runway/taxiway edge and approach lighting, ideally at night, or review the current unserviceable-light log; scan for dark or damaged fixtures, specifically checking whether any two adjacent lights are both unserviceable. Pass: log actively maintained, no two adjacent lights out. Fail: no log kept, or adjacent lights unserviceable. 2. Where feasible, request a live changeover demonstration; check the test date isn't stale — batteries and generators can drift out of spec with age. Pass: recent test on file, measured time within the required limit. Fail: no re-test since installation, or a measured time exceeding the requirement. | 1. AGL system's unserviceable-light log/register showing repair turnaround times; any NOTAM history triggered by AGL unserviceability. 2. Standby generator/UPS changeover-time test records for lighting circuits, benchmarked against the requirement for the runway's approach category. |  | AGL outage limits (Asset) and standby changeover records (Document) in one row
KSIA-PSR-025 | Process Safety & Risk | Statutory Appointments & Competencies | Electrical appointments & competencies | Fire Detection | Evidence + Site Physical Verification + Question | Practice | examine | The question is the crux: does servicing include actual detector-head functional testing, or only panel and battery checks. A full service record of the wrong service is still non-compliant. | Check the fire control/indicating panel for current status and fault indications. Ask for a demonstration or recent record of an actual detector-head/call-point functional test, and compare the detection zone layout against commissioning documentation where alterations may have occurred. Pass: current commissioning certificate, functional detector-level test records, SAQCC Fire-registered contractor. Fail: only panel/battery checks on record, or zones no longer matching the as-built layout. | Fire detection system's commissioning certificate; periodic service/test records; confirmation the maintenance contractor is SAQCC Fire-registered; ACSA's D080 002M procedure for the specific required frequency.
KSIA-PSR-026 | Process Safety & Risk | Statutory Appointments & Competencies | Civil appointments & competencies | Water usage and storm water drainage | Evidence + Site Physical Verification | Document | reconcile | A Water Use Licence or documented General Authorisation basis; the walk identifies the actual discharge points and matches them to what is authorised. | 1. Physically identify the site's stormwater discharge points and confirm they match what's described/authorised in the licence or exemption assessment. Pass: current WUL, or a documented, reasoned GA exemption assessment matching the actual discharge points. Fail: no licence and no documented exemption assessment — status simply assumed. 2. Inspect oil-water separators and containment bunding at fuel and de-icing areas for visible condition, overflow/leakage signs, and evidence of scheduled desludging; check the plan reflects the current site layout. Pass: separators/containment visibly maintained on a documented schedule, plan matches site reality. Fail: separators shown on drawings only with no inspection schedule, or an outdated plan. | 1. The Water Use Licence, or a documented basis for a General Authorisation exemption, for stormwater discharge points. 2. The airport's stormwater management plan; maintenance/inspection records for oil-water separators and fuel/de-icing area containment; any discharge quality monitoring results.
KSIA-PSR-027 | Process Safety & Risk | Statutory Appointments & Competencies | Civil appointments & competencies | RWY friction testing and rubber removal | Evidence + Site Physical Verification | Document | none | Friction test reports against the applicable minimum, at the frequency for that runway's traffic, with the device's calibration certificate. All desk work. | — nothing to inspect on site | 1. ACSA's D060 010 Friction Testing Procedure; continuous friction-measuring device test reports/logs per runway, dated and compared against the applicable minimum; the device's own calibration certificate. 2. Rubber-removal work records (method and date), tied to the friction test results that triggered them.
KSIA-PSR-028 | Process Safety & Risk | Statutory Appointments & Competencies | B&FM appointments & competencies | Asbestos register | Evidence + Site Physical Verification | Document | reconcile | Register reviewed within 24 months with ACM locations on floor plans; the walk confirms warning labels are where the register says. | Cross-check the register's floor-plan locations against a physical walk of the marked areas — confirm ACM warning labels/signage are present where the register says they should be, and that the recorded condition/management strategy matches what's visibly there. Pass: register current (reviewed within 24 months), signage matches register. Fail: overdue review, missing signage, or ACM altered since the last review without an update. | Current asbestos register/inventory (last review date, must be within 24 months); floor plans marking ACM locations; risk categorisation and management strategy per item; evidence of distribution to employees/contractors (and a new owner, on sale).
KSIA-PSR-029 | Process Safety & Risk | Statutory Appointments & Competencies | All Disciplines | Covid 19 regulations compliance | Evidence + Question | Document | none | A workplace plan, if one is still maintained. | — nothing to inspect on site | ACSA's current Covid-19/communicable disease workplace plan (if still maintained) and any current risk assessment addressing SARS-CoV-2 as a Group 3 biological agent. | the row's own question asks whether this requirement is still live at all — it may be obsolete
KSIA-PSR-030 | Process Safety & Risk | Statutory Appointments & Competencies | Other appointments & competencies | Sustainability | Site Physical Verification + Question | Document | examine | Provisional. The row does not say what it tests. | If ISO 14001 alignment is claimed, look for a certification plaque/certificate or visible EMS documentation/signage on site. | Evidence for whatever 'Sustainability' is being tested — GBCSA certification at the 4 Star minimum, the business case with IRR, NPV, profitability index and payback, the 36-month maintenance schedule, FMEA and RAM studies, and operations and maintenance competency records against D100MAN cl. 4's targets (99.5% availability, 20-year design life, power factor 0.95, >40% saving on retrofits). NOTE: the requirement is a single word and is not an appointment or a competency — it does not belong in this asset system. | NO evidence stated the row's own question asks what this line is meant to test — ISO 14001, an internal policy, or something else. It cannot be audited as written.
KSIA-PSR-031 | Process Safety & Risk | Statutory Appointments & Competencies | Other appointments & competencies | Risk management | Evidence + Question | Document | none | Board-approved policy, current register, committee minutes evidencing review. | — nothing to inspect on site | Board-approved risk management policy/strategy and current risk register; Risk Committee or Audit & Risk Committee minutes evidencing regular review. | the row's own question asks whether this is enterprise risk management or plant-level OHS risk assessment — two different auditees
KSIA-PSR-032 | Process Safety & Risk | Statutory Appointments & Competencies | Other appointments & competencies | Asset operation and reliability | Evidence + Site Physical Verification + Question | Document | examine | ISO 55001 documents if alignment is claimed, otherwise planned preventive maintenance records. | Where ISO 55001 alignment is claimed, look for asset tagging/identification on the physical asset consistent with a formal asset register. Otherwise check the asset's physical condition against any available condition score or inspection record, and note visible breakdown/repair history (maintenance stickers, logbooks) as a cross-check against reported KPIs. | If ISO 55001 alignment is claimed: Asset Management Policy, Strategic Asset Management Plan (SAMP), asset register, management review records. If not: planned preventive-maintenance completion-rate reports, breakdown/downtime logs, and reliability KPIs (availability, MTBF) actually tracked for the audited asset. | the row's own question asks which of the two it is — the evidence required differs completely
KSIA-PSR-033 | Process Safety & Risk | Statutory Appointments & Competencies | Other appointments & competencies | Asset renewal programme | Evidence + Site Physical Verification | Document | examine | The renewal programme and its capital linkage; the finding is a visibly deteriorated asset that does NOT appear on it. | Where an asset observed on site appears visibly aged, worn or near end-of-life, check whether it appears on the renewal programme with a planned renewal date — a visibly deteriorated asset with no renewal plan on file is a red flag. | Current asset renewal/replacement programme or plan, showing which assets/asset classes are due for renewal and over what timeframe, and its linkage to the approved capital budget.
KSIA-PSR-034 | Process Safety & Risk | Statutory Appointments & Competencies | Appointments | GMR 2(1), 16(2), electrical (EIR/EMR) and LI/LMI appointments in writing, current, with competency evidence. | Evidence + Site Physical Verification | Document | reconcile | Appointment letters current with competency evidence; the walk confirms the named person is the one performing the role. | 1. Confirm the person named in the GMR 2(1) letter is the one actually performing the supervisory role, evidenced by inspection/SOP/permit records bearing their name. 2. Confirm the named GMR 16(2) appointee is the one actually responsible on site, evidenced by inspection/maintenance sign-off records. 3. Confirm the named EIR/EMR appointees match the people actually responsible for electrical installations/machinery on site. 4. Confirm the named LI/LMI appointee is the one actually inspecting/controlling lifting machinery on site, evidenced by inspection records. | Written appointments for GMR 2(1) on OHS 008, GMR 2(7) on OHS 009, Section 16(2) on OHS 001, supervisors on OHS 002 and the electrical EIR/EMR and LI/LMI roles, each inside its three-year validity, carrying all four mandatory content elements, with the competency evidence the role requires — at or above 11kV the GMR 2(1) appointee needs a recognised Engineering Qualification AND the legislative training — and the named person actually performing the role, evidenced by inspection, SOP or permit records bearing their name. | evidence stub: 'Appointment letters; certificates' | GMR 2(1), 16(2), EIR/EMR and LI/LMI are four separate statutory appointments in one row
KSIA-PSR-035 | Process Safety & Risk | Statutory Appointments & Competencies | Training & standby | Training matrix (trade tests, wireman's licence, LPG, working at heights), standby rosters and call-out records. | Evidence + Site Physical Verification + Question | Document | reconcile | Training matrix and rosters; the walk spot-checks staff doing height, gas or electrical work against a current matching competency. | 1. Spot-check a sample of staff performing height, gas, or electrical work on site against the training matrix for a current, matching competency. 2. Where possible, confirm today's listed standby person is actually contactable/available. | A training matrix completed with the Line Manager covering trade tests, wireman's licence, LPG and working at heights, with OHS induction inside 30 days of commencing work, on-the-job training inside 30 days of employment or transfer, GMR 2(1) and 2(7) legislative training inside 6 months of appointment; standby rosters and call-out records; and a sample of staff doing height, gas or electrical work on site holding a current matching competency. | evidence stub: 'Training matrix; rosters'
KSIA-PSR-036 | Process Safety & Risk | Contractor & Permit Management | Contractors | Contractor s37(2) agreements, safety files, permit-to-work & hot-work permits, induction records for maintenance contractors. | Evidence + Site Physical Verification + Question | Practice | reconcile | Tests whether the arrangement holds — is work stopped when a s37(2) agreement lapses, do inductions expire. The filed agreement proves only that one was signed. | 1. Confirm the contractor(s) observed working on site match the names on the filed s37(2) agreements. 2. Ask a contractor team on site to produce their safety file, and check it matches the work actually being observed. 3. Where hot work or permit-controlled work is in progress, ask to see the live permit at the work location and confirm it matches the task, location and time. Pass: a valid, matching permit is displayed. Fail: work proceeding without one. 4. Spot-check contractor workers on site on whether and when they were inducted, against the induction register. | A Section 37(2) mandatary agreement OHS 040 for every contractor on site, a SHE File submitted at least 14 days before commencement and reviewed within 7 working days scoring at least 90% on OHS 037 for high-risk work, permit-to-work and hot-work permits for the work actually in progress, induction records — and the contractor teams observed on site matching the names on the filed agreements. | evidence stub: 'Agreements; safety files; permits'
KSIA-PSR-037 | Process Safety & Risk | Incident Management | Reporting | Incidents/near-misses recorded, s24 reportable incidents reported, investigations and corrective actions closed; trend reviewed. | Evidence + Site Physical Verification + Question | Practice | none | Ask maintenance staff how they report a near-miss and check those examples are in the register. A mismatch is the finding, and no document shows it. | — nothing to inspect on site | An incident register with near-misses in it, notification inside ACSA's clock (12 hours for a fatality, 24 hours for a Section 24 injury or LTI, 36 hours for Section 24(c) equipment failure, 72 hours for a near miss), Annexure 1 submitted to the DoL, investigations closed with their corrective actions, and a trend review. The real test is asking maintenance staff how they report a near-miss and finding the examples they describe in the register. | evidence stub: 'Incident register'

## Gaps
ID | Discipline | Asset system | Kind | What is wrong with the check as written
KSIA-ELE-004 | Electrical | AGL | Evidence not stated | NO evidence stated
KSIA-ELE-006 | Electrical | AGL | The question does the check's work | the row's own question asks what the aerodrome's certified lighting category IS — the limit cannot be applied without it
KSIA-ELE-009 | Electrical | AGL | Evidence not stated | evidence stub: 'Inspection & test records'
KSIA-ELE-010 | Electrical | Electricity Distribution System | Evidence not stated | NO evidence stated
KSIA-ELE-011 | Electrical | Electricity Distribution System | Evidence not stated | evidence stub: 'Drawings; protection study'
KSIA-ELE-012 | Electrical | Electricity Distribution System | Evidence not stated | evidence stub: 'Cable records; inspection'
KSIA-ELE-013 | Electrical | Electricity Distribution System | Evidence not stated | evidence stub: 'Load readings; SLD verification'
KSIA-ELE-017 | Electrical | Switchgear | Evidence not stated | evidence stub
KSIA-ELE-018 | Electrical | Substations | Evidence not stated | NO evidence stated
KSIA-ELE-020 | Electrical | Substations | Evidence not stated | NO evidence stated
KSIA-ELE-022 | Electrical | Substations | Evidence not stated | NO evidence stated
KSIA-ELE-023 | Electrical | Substations | Evidence not stated | evidence stub: 'Site inspection'
KSIA-ELE-024 | Electrical | Substations | Evidence not stated | evidence stub: 'Test reports'
KSIA-ELE-026 | Electrical | Generators | The question does the check's work | the row's own question asks whether leak detection is by actual pressure test or only consumption reconciliation — those are different assurances
KSIA-ELE-030 | Electrical | Generators | Evidence not stated | evidence stub: "Physical inspection; drawings"
KSIA-ELE-031 | Electrical | Generators | Evidence not stated | evidence stub: 'Generator test logs'
KSIA-ELE-032 | Electrical | Generators | Evidence not stated | evidence stub: 'ATS test records'
KSIA-ELE-033 | Electrical | Generators | Evidence not stated | evidence stub
KSIA-ELE-034 | Electrical | Transformers | The question does the check's work | the row's own question asks whether DGA was actually done or only basic tests — a different assurance
KSIA-ELE-035 | Electrical | Transformers | Evidence not stated | evidence stub: 'Inspection records'
KSIA-ELE-036 | Electrical | UPS | Evidence not stated | evidence stub
KSIA-ELE-041 | Electrical | Lighting | Evidence not stated | evidence stub: 'Lux measurements; inspection'
KSIA-ELE-042 | Electrical | Emergency Lighting | Evidence not stated | evidence stub: 'Test register'
KSIA-ELE-043 | Electrical | FDS & Gaseous Suppression | Evidence not stated | evidence stub
KSIA-ELE-044 | Electrical | X-Ray Machines | Evidence not stated | evidence stub: 'Licence; survey reports'
KSIA-ELE-045 | Electrical | Earthing & Lightning Protection | Evidence not stated | evidence stub: 'Test certificates'
KSIA-ELE-048 | Electrical | General Electrical Installation | Evidence not stated | NO evidence stated
KSIA-MEC-001 | Mechanical | HVAC | No threshold to test against | ACSA requires only a six-monthly MOTOR RUNNING CURRENT — no air-flow rate, velocity or L/s figure anywhere in D080 025M. The check asks for a test ACSA's own manual does not call for.
KSIA-MEC-002 | Mechanical | HVAC | No threshold to test against | ACSA states no extraction rate or air-change requirement — only motor running current
KSIA-MEC-003 | Mechanical | HVAC | No threshold to test against | ACSA's threshold is a 3-monthly auxiliary activation test, not a flow rate
KSIA-MEC-005 | Mechanical | HVAC | No threshold to test against | no acsaThreshold — no monthly roof-vent test interval is stated anywhere in the source
KSIA-MEC-008 | Mechanical | HVAC | No threshold to test against | no acsaThreshold at all — SANS 10147 cl. 6.1.6.1 is named in the evidence but no ACSA interval is quoted
KSIA-MEC-012 | Mechanical | HVAC | Other | no standalone earth-leakage test interval in ACSA — it rides on the yearly COC cycle
KSIA-MEC-012 | Mechanical | HVAC | Duplicate or overlap | this identical check appears six times in the register: MEC-012, 052, 064, 087, 092, 102
KSIA-MEC-014 | Mechanical | HVAC | Noted — nothing to inspect, correctly | no walkabout text at all, correctly
KSIA-MEC-016 | Mechanical | HVAC | Duplicate or overlap | verbatim duplicate of MEC-105 — same requirement, evidence and walkabout, one filed under HVAC and one under Water Treatment Plant
KSIA-MEC-017 | Mechanical | HVAC | Evidence not stated | evidence stub: 'Plant logs; PER certificates'
KSIA-MEC-017 | Mechanical | HVAC | Duplicate or overlap | overlaps MEC-007 (PER certificates) and MEC-013 (refrigerant leak log)
KSIA-MEC-018 | Mechanical | HVAC | Evidence not stated | evidence stub: 'Treatment & test records'
KSIA-MEC-018 | Mechanical | HVAC | Duplicate or overlap | overlaps MEC-008, whose evidence is the same Legionella certificates
KSIA-MEC-021 | Mechanical | People Movers | No threshold to test against | ACSA's threshold here is a MONTHLY check of the reports, which is a different obligation from holding a valid Annexure A
KSIA-MEC-023 | Mechanical | People Movers | No threshold to test against | no acsaThreshold — platform stairlifts are not in D080 020M's inspection tables at all
KSIA-MEC-027 | Mechanical | People Movers | Duplicate or overlap | duplicates the CoC pattern of MEC-009, 031, 052, 064, 089, 094, 101
KSIA-MEC-028 | Mechanical | People Movers | Evidence not stated | evidence stub: 'LI certificates; register'
KSIA-MEC-028 | Mechanical | People Movers | Duplicate or overlap | duplicates MEC-019 through MEC-027
KSIA-MEC-029 | Mechanical | People Movers | Evidence not stated | evidence stub: 'Site inspection'
KSIA-MEC-031 | Mechanical | Passenger Boarding Bridges (PLBs) | No threshold to test against | requirement is one word, 'COC' — no scope, no interval, no issuing authority stated in the check itself
KSIA-MEC-032 | Mechanical | Passenger Boarding Bridges (PLBs) | Conflict in the source | conflicting intervals in the source: FALE's own cycle is 2-yearly in years 2 and 4, against a counter-benchmark of a three-monthly visual structural inspection
KSIA-MEC-033 | Mechanical | Passenger Boarding Bridges (PLBs) | Evidence not stated | evidence stub: 'PrEng structural assessment report'
KSIA-MEC-033 | Mechanical | Passenger Boarding Bridges (PLBs) | No threshold to test against | ACSA's own manual requires NO such report — the register's acsaEvidence field says '(none required by D080 029M)'. The check demands evidence ACSA does not oblige anyone to hold.
KSIA-MEC-033 | Mechanical | Passenger Boarding Bridges (PLBs) | Duplicate or overlap | duplicates MEC-032
KSIA-MEC-034 | Mechanical | Passenger Boarding Bridges (PLBs) | Evidence not stated | evidence stub: 'PM records; operator register'
KSIA-MEC-034 | Mechanical | Passenger Boarding Bridges (PLBs) | Duplicate or overlap | overlaps MEC-030, which tests the same four systems from the record side
KSIA-MEC-036 | Mechanical | Fuel System | Conflict in the source | requirement says 3-yearly but ACSA requires the plan TESTED at least every 12 months and SUBMITTED to NERSA annually — three different clocks in one check
KSIA-MEC-037 | Mechanical | Fuel System | Conflict in the source | DIRECT CONFLICT: the check says 3-yearly, ACSA D060 021M cl. 4.17.5 says the hydrant line pressure test at FALE (King Shaka) is YEARLY. Auditing FALE against 3 years would pass an installation that is two years overdue.
KSIA-MEC-038 | Mechanical | Fuel System | Conflict in the source | CONFLICTING CODE: the check names ASME B31.3; ACSA D060 021M cl. 4.15.1 names API/IP 1540 plus JIG. No wall-thickness or design criterion is stated for either.
KSIA-MEC-039 | Mechanical | Fuel System | Wrong content on the row | 'potable gas meters' — almost certainly PORTABLE gas meters; the register carries the typo
KSIA-MEC-039 | Mechanical | Fuel System | Other | ACSA names four calibration items (crawl beams, gauges, hydrocarbon detectors, tightness control system) and NO quarterly interval
KSIA-MEC-040 | Mechanical | Fuel System | No threshold to test against | ACSA does not define 'ESB'; the manual's term is ESD, maintained six-monthly at FALE. The check and the manual may not be describing the same device.
KSIA-MEC-042 | Mechanical | Fuel System | No threshold to test against | the -850 mV CSE criterion is in the check's evidence but nowhere in ACSA's threshold — ACSA states intervals only
KSIA-MEC-043 | Mechanical | Fuel System | Other | no coating inspection interval and no holiday-test criterion in ACSA
KSIA-MEC-043 | Mechanical | Fuel System | More than one check in the row | the check may be unanswerable in an audit period with no excavation — it needs an explicit 'not applicable this period' outcome rather than a fail
KSIA-MEC-044 | Mechanical | Fuel System | Duplicate or overlap | duplicates MEC-046 (lids) and MEC-054 (couplers, seals, lids, water)
KSIA-MEC-045 | Mechanical | Fuel System | No threshold to test against | ACSA notes 'leak rate is to be noted but NO numeric limit' — the check has no pass mark to test against
KSIA-MEC-046 | Mechanical | Fuel System | No threshold to test against | no acsaThreshold for anodising, seal condition or lid functionality — daily inspection is required but no criterion is given
KSIA-MEC-046 | Mechanical | Fuel System | Duplicate or overlap | duplicates MEC-044 and MEC-054
KSIA-MEC-047 | Mechanical | Fuel System | No threshold to test against | no acsaThreshold at all for a dynamic closing test
KSIA-MEC-048 | Mechanical | Fuel System | No threshold to test against | ACSA's calibration list names Gauges but not custody-transfer meter proving; no annual proving interval is stated
KSIA-MEC-049 | Mechanical | Fuel System | No threshold to test against | API 653 is named in the check's evidence but not by ACSA — ACSA requires five-yearly CLEANING, which is a different operation from an integrity inspection
KSIA-MEC-050 | Mechanical | Fuel System | No threshold to test against | no acsaThreshold — SANS 10108 is named only in the check's own evidence field
KSIA-MEC-051 | Mechanical | Fuel System | Duplicate or overlap | overlaps MEC-053, which reads the same nameplates for the same zones
KSIA-MEC-052 | Mechanical | Fuel System | More than one check in the row | three checks in one requirement, each already asked separately elsewhere
KSIA-MEC-052 | Mechanical | Fuel System | Duplicate or overlap | duplicates MEC-012, MEC-010 and MEC-009 respectively
KSIA-MEC-054 | Mechanical | Fuel System | Evidence not stated | evidence stub: 'Pit inspection register; site walk'
KSIA-MEC-054 | Mechanical | Fuel System | Duplicate or overlap | duplicates MEC-044 and MEC-046
KSIA-MEC-055 | Mechanical | Fuel System | Evidence not stated | evidence stub: 'Test records'
KSIA-MEC-055 | Mechanical | Fuel System | Duplicate or overlap | duplicates MEC-037 (pressure test), MEC-040 (ESD) and MEC-045 (tightness)
KSIA-MEC-055 | Mechanical | Fuel System | No threshold to test against | bonding at fuelling positions appears nowhere else and has no ACSA threshold — it is the only new content in the row
KSIA-MEC-056 | Mechanical | Fuel System | Evidence not stated | evidence stub: 'Inspection certificates'
KSIA-MEC-056 | Mechanical | Fuel System | Duplicate or overlap | overlaps MEC-049 for tank integrity
KSIA-MEC-056 | Mechanical | Fuel System | More than one check in the row | four unrelated things in one row: tank inspection, bund integrity, filter/separator maintenance, product quality
KSIA-MEC-058 | Mechanical | BHS | Duplicate or overlap | overlaps MEC-057, MEC-062 and MEC-065 — four checks walking the same conveyor guarding
KSIA-MEC-059 | Mechanical | BHS | No threshold to test against | no acsaThreshold — no siren duration or margin before motion is stated anywhere
KSIA-MEC-059 | Mechanical | BHS | Duplicate or overlap | duplicates MEC-063 for the sorter
KSIA-MEC-062 | Mechanical | BHS | Duplicate or overlap | duplicates MEC-057 and MEC-058
KSIA-MEC-063 | Mechanical | BHS | Duplicate or overlap | duplicates MEC-059
KSIA-MEC-064 | Mechanical | BHS | Duplicate or overlap | duplicates MEC-012 (earth leakage) and MEC-010 (wiring diagrams and CoC)
KSIA-MEC-065 | Mechanical | BHS | Evidence not stated | evidence stub: 'CMMS PM reports'
KSIA-MEC-065 | Mechanical | BHS | Duplicate or overlap | duplicates MEC-057, MEC-058 and MEC-060
KSIA-MEC-065 | Mechanical | BHS | More than one check in the row | three different check types in one row
KSIA-MEC-067 | Mechanical | Fire Protection - Fire Extinguishers | Conflict in the source | ACSA requires inspection QUARTERLY; the check's evidence asks for a MONTHLY visual log — two different intervals in one check
KSIA-MEC-068 | Mechanical | Fire Protection - Fire Extinguishers | Evidence not stated | evidence stub: 'Service tags; register'
KSIA-MEC-068 | Mechanical | Fire Protection - Fire Extinguishers | Duplicate or overlap | duplicates MEC-066 and MEC-067
KSIA-MEC-075 | Mechanical | Fire Protection - Hose reels and fire hydrants | Conflict in the source | CONFLICT: the check says 3-yearly, ACSA D080 002M cl. 4.7.8 says deluge/control valve service records YEARLY
KSIA-MEC-076 | Mechanical | Fire Protection - Hose reels and fire hydrants | No threshold to test against | ACSA qualifies this '(if applicable)' and never says when it applies — the check has no applicability rule
KSIA-MEC-077 | Mechanical | Fire Protection - Hose reels and fire hydrants | Evidence not stated | evidence stub: 'Test records'
KSIA-MEC-077 | Mechanical | Fire Protection - Hose reels and fire hydrants | Duplicate or overlap | duplicates MEC-071 and MEC-072
KSIA-MEC-077 | Mechanical | Fire Protection - Hose reels and fire hydrants | Conflict in the source | INTERVAL CONFLICT: the check says annual flow/pressure tests; ACSA requires valve station flow and pressure tests MONTHLY
KSIA-MEC-082 | Mechanical | Fire Protection - Fire Water pump station | Duplicate or overlap | overlaps MEC-080 in practice — the two are commonly recorded as one test
KSIA-MEC-085 | Mechanical | Fire Protection - Fire Water pump station | Evidence not stated | evidence stub: 'Test logs'
KSIA-MEC-085 | Mechanical | Fire Protection - Fire Water pump station | Duplicate or overlap | duplicates MEC-078 through MEC-084
KSIA-MEC-085 | Mechanical | Fire Protection - Fire Water pump station | No threshold to test against | introduces two terms — 'churn test' and 'jockey pump' — that appear nowhere else in the register and have no ACSA threshold
KSIA-MEC-086 | Mechanical | Sewer, Potable & Stormwater Pumps | No threshold to test against | no acsaThreshold — no gas monitor calibration interval is stated
KSIA-MEC-087 | Mechanical | Sewer, Potable & Stormwater Pumps | Duplicate or overlap | fifth of six near-identical earth-leakage rows: MEC-012, 052, 064, 087, 092, 102
KSIA-MEC-089 | Mechanical | Sewer, Potable & Stormwater Pumps | Duplicate or overlap | duplicates MEC-010 and MEC-009 scoped to a different panel; the same pair recurs at MEC-052, 064, 094 and 101
KSIA-MEC-090 | Mechanical | Sewer, Potable & Stormwater Pumps | Evidence not stated | evidence stub: 'PM & alarm records'
KSIA-MEC-091 | Mechanical | Gas Hot Water Facility | Duplicate or overlap | WRONG SYSTEM: the requirement, evidence and walkabout all say SEWER SUMP and confined-space entry, filed under Gas Hot Water Facility. This is a copy of MEC-086 pasted into the wrong asset system.
KSIA-MEC-091 | Mechanical | Gas Hot Water Facility | Other | if a gas monitor is genuinely required at a gas hot water facility it would be for LPG/combustible gas, which is a different instrument and a different configuration from H2S/LEL/O2
KSIA-MEC-092 | Mechanical | Gas Hot Water Facility | Duplicate or overlap | sixth of six near-identical earth-leakage rows
KSIA-MEC-093 | Mechanical | Gas Hot Water Facility | Wrong content on the row | evidence text says 'pump couplings, shafts' — copied from MEC-088 (Sewer Pumps) without re-scoping to what actually rotates in a gas hot water facility
KSIA-MEC-093 | Mechanical | Gas Hot Water Facility | No threshold to test against | the acsaThreshold cited is from Air Handling Units (D080 025M cl. 4.4.5), a third unrelated system
KSIA-MEC-094 | Mechanical | Gas Hot Water Facility | Duplicate or overlap | fifth of five near-identical wiring-diagram-and-CoC rows
KSIA-MEC-095 | Mechanical | Gas Hot Water Facility | Evidence not stated | evidence stub: 'CoC; inspection'
KSIA-MEC-095 | Mechanical | Gas Hot Water Facility | Wrong content on the row | this is the ONLY substantive check in the Gas Hot Water Facility system — the other four (091-094) are copy-pastes from other systems
KSIA-MEC-099 | Mechanical | Water Treatment Plant | No threshold to test against | no acsaThreshold — the control hierarchy has no stated criterion here
KSIA-MEC-101 | Mechanical | Water Treatment Plant | Duplicate or overlap | fourth of five near-identical wiring-diagram-and-CoC rows
KSIA-MEC-102 | Mechanical | Water Treatment Plant | Duplicate or overlap | sixth near-identical earth-leakage row
KSIA-MEC-105 | Mechanical | Water Treatment Plant | Duplicate or overlap | verbatim duplicate of MEC-016 — identical requirement, evidence and walkabout
KSIA-MEC-106 | Mechanical | Water Treatment Plant | Evidence not stated | evidence stub: 'Lab results; cleaning records'
KSIA-MEC-112 | Mechanical | Façade Access & Lifting Equipment | Noted — nothing to inspect, correctly | no walkabout text at all, correctly
KSIA-MEC-112 | Mechanical | Façade Access & Lifting Equipment | No threshold to test against | no acsaThreshold
KSIA-MEC-113 | Mechanical | Façade Access & Lifting Equipment | Evidence not stated | evidence stub: 'LMI certificates; register'
KSIA-MEC-113 | Mechanical | Façade Access & Lifting Equipment | Duplicate or overlap | duplicates MEC-107, MEC-108 and MEC-110
KSIA-CIV-002 | Civil | Markings | No threshold to test against | no acsaThreshold — D060 009M defers dimensions to ICAO Annex 14 and the as-builts, so the figure lives in a drawing this register does not name
KSIA-CIV-003 | Civil | Markings | Duplicate or overlap | overlaps CIV-001 almost entirely — 001 is 'conspicuous condition', 003 is 'visibility'
KSIA-CIV-006 | Civil | Markings | More than one check in the row | bundles four attributes (visibility, dimensions, colour, background) into one pass/fail
KSIA-CIV-007 | Civil | Markings | Evidence not stated | evidence stub: 'Inspection; programme'
KSIA-CIV-007 | Civil | Markings | Duplicate or overlap | duplicates CIV-001 through CIV-006
KSIA-CIV-008 | Civil | Visual Aids | Duplicate or overlap | exact duplicate of CIV-001 — same requirement text, same evidenceExpected, same walkabout
KSIA-CIV-010 | Civil | Visual Aids | Conflict in the source | conflicting threshold in the source: signage inspection Daily (D060 001M cl. 4.9.23) versus Monthly (D060 014M cl. 4.7.8)
KSIA-CIV-011 | Civil | Visual Aids | More than one check in the row | bundles four unrelated asset types — signs, PAPI, wind indicators, obstacle marking/lighting — plus a document (the obstacle survey)
KSIA-CIV-011 | Civil | Visual Aids | Evidence not stated | evidence stub: 'Inspection; obstacle survey'
KSIA-CIV-012 | Civil | Wind Direction Indicator | Evidence not stated | evidence stub: 'Site inspection'
KSIA-CIV-016 | Civil | Runway | Duplicate or overlap | overlaps CIV-025, which asks the same question with the PCI survey as its evidence
KSIA-CIV-018 | Civil | Runway | No threshold to test against | no threshold anywhere in the source for how big a step is a failure — the check has no pass mark
KSIA-CIV-019 | Civil | Runway | Duplicate or overlap | overlaps CIV-016 (surface defects) and CIV-018 (edge flush) — three checks walking the same 10 cm of pavement
KSIA-CIV-022 | Civil | Runway | Evidence not stated | no acsaThreshold and no ACSA evidence named at all — the CBR figure and the RFF trafficability standard are not in the register
KSIA-CIV-023 | Civil | Runway | More than one check in the row | two different checks in one: frangibility of authorised objects, and the presence of unauthorised ones
KSIA-CIV-024 | Civil | Runway | Evidence not stated | evidence stub: 'Friction test reports; action records'
KSIA-CIV-024 | Civil | Runway | Duplicate or overlap | overlaps CIV-026 almost exactly
KSIA-CIV-025 | Civil | Runway | Evidence not stated | evidence stub: 'PCI survey; work orders'
KSIA-CIV-025 | Civil | Runway | Duplicate or overlap | overlaps CIV-016, CIV-017 and CIV-019
KSIA-CIV-026 | Civil | Friction Measurement & Corrective Maintenance | Duplicate or overlap | duplicates CIV-024 — one is under Runway/Friction, the other under its own asset system
KSIA-CIV-027 | Civil | Friction Measurement & Corrective Maintenance | Noted — nothing to inspect, correctly | no walkabout text at all, correctly
KSIA-CIV-028 | Civil | Friction Measurement & Corrective Maintenance | Noted — nothing to inspect, correctly | no walkabout text at all, correctly
KSIA-CIV-028 | Civil | Friction Measurement & Corrective Maintenance | Duplicate or overlap | overlaps CIV-024, whose evidence is the same reports
KSIA-CIV-029 | Civil | Friction Measurement & Corrective Maintenance | Noted — nothing to inspect, correctly | no walkabout text at all
KSIA-CIV-030 | Civil | Taxiways & Taxilanes | Duplicate or overlap | identical requirement text to CIV-013 and CIV-039 — the register repeats the pavement condition set once per surface type
KSIA-CIV-031 | Civil | Taxiways & Taxilanes | No threshold to test against | requirement asserts 'taxiway strength to be equal to that of runways' with no source named for that rule
KSIA-CIV-032 | Civil | Taxiways & Taxilanes | Wrong content on the row | walkabout text says 'Walk the runway' — copied from CIV-016 and not re-scoped
KSIA-CIV-032 | Civil | Taxiways & Taxilanes | Duplicate or overlap | duplicates CIV-016 and CIV-041
KSIA-CIV-033 | Civil | Taxiways & Taxilanes | Duplicate or overlap | duplicates CIV-017 and CIV-042
KSIA-CIV-034 | Civil | Taxiways & Taxilanes | No threshold to test against | no threshold for the size of a failing step, same as CIV-018
KSIA-CIV-035 | Civil | Taxiways & Taxilanes | Duplicate or overlap | duplicates CIV-019
KSIA-CIV-037 | Civil | Taxiways & Taxilanes | Duplicate or overlap | duplicates CIV-021
KSIA-CIV-038 | Civil | Taxiways & Taxilanes | Evidence not stated | evidence stub: 'Inspection reports'
KSIA-CIV-038 | Civil | Taxiways & Taxilanes | Duplicate or overlap | duplicates CIV-030, 032, 034, 035 and the taxiway centreline marking is already CIV-001/003
KSIA-CIV-039 | Civil | Aprons | Duplicate or overlap | duplicates CIV-013 and CIV-030
KSIA-CIV-041 | Civil | Aprons | Wrong content on the row | walkabout text says 'Walk the runway' — copied from CIV-016 and not re-scoped
KSIA-CIV-041 | Civil | Aprons | Duplicate or overlap | duplicates CIV-016 and CIV-032
KSIA-CIV-042 | Civil | Aprons | Duplicate or overlap | duplicates CIV-017 and CIV-033
KSIA-CIV-043 | Civil | Aprons | Duplicate or overlap | duplicates CIV-018 and CIV-034
KSIA-CIV-045 | Civil | Aprons | Evidence not stated | evidence stub: 'Inspection; spill records'
KSIA-CIV-045 | Civil | Aprons | More than one check in the row | three different check types in one: surface condition (Asset), spill clean-up procedure (Practice), tie-down and grounding point condition (Asset)
KSIA-CIV-047 | Civil | Pavement Strength | Evidence not stated | evidence stub: 'Pavement evaluation; AIP entry'
KSIA-CIV-047 | Civil | Pavement Strength | No threshold to test against | says PCN, which ICAO replaced with PCR — the register is on the old vocabulary here while CIV-014 uses PCR
KSIA-CIV-047 | Civil | Pavement Strength | Duplicate or overlap | duplicates CIV-014 and CIV-046
KSIA-CIV-051 | Civil | Drainage | Evidence not stated | evidence stub: 'Inspection register'
KSIA-CIV-051 | Civil | Drainage | Duplicate or overlap | duplicates CIV-050 for the drains; overlaps CIV-017/033/042 for the ponding
KSIA-CIV-053 | Civil | Inspections | Noted — nothing to inspect, correctly | no walkabout text at all, correctly
KSIA-CIV-054 | Civil | Inspections | Evidence not stated | evidence stub: "Inspection logs"
KSIA-CIV-054 | Civil | Inspections | Duplicate or overlap | duplicates CIV-052 for the daily inspection frequency
KSIA-CIV-055 | Civil | Airside Service Roads & Perimeter | Evidence not stated | evidence stub: "Site inspection; work orders"
KSIA-CIV-055 | Civil | Airside Service Roads & Perimeter | More than one check in the row | bundles pavement condition, signage and markings — the same three the runway gets as separate checks
KSIA-CIV-056 | Civil | Perimeter / Security Fence | Evidence not stated | evidence stub: 'Inspection records'
KSIA-CIV-056 | Civil | Perimeter / Security Fence | More than one check in the row | bundles fence condition (Asset), clear zones (Asset), patrol records (Document) and gate/access-control function (Asset)
KSIA-BFM-006 | Building & Facilities | Certificates | Evidence not stated | evidence stub: 'Certificate file'
KSIA-BFM-010 | Building & Facilities | Roofs & Waterproofing | Evidence not stated | evidence stub: 'Inspection; work orders'
KSIA-BFM-012 | Building & Facilities | Building Drainage | The question does the check's work | the row's own question asks whether they are accessible to the SITE team or only at head office — that is a different test from whether they exist
KSIA-BFM-017 | Building & Facilities | Building Drainage | Evidence not stated | evidence stub
KSIA-BFM-023 | Building & Facilities | Water & Plumbing | The question does the check's work | the row's own question asks whether the supply is municipal or ACSA-operated — the sampling obligation differs completely
KSIA-BFM-024 | Building & Facilities | Water & Plumbing | Evidence not stated | evidence stub: 'Inspection; maintenance records'
KSIA-BFM-024 | Building & Facilities | Water & Plumbing | The question does the check's work | the row's own question asks whether ACSA has a defined temperature standard at all
KSIA-BFM-026 | Building & Facilities | Refuse Disposal | Evidence not stated | NO evidence stated
KSIA-BFM-030 | Building & Facilities | Refuse Disposal | Evidence not stated | evidence stub: 'Waste manifests; contracts'
KSIA-BFM-031 | Building & Facilities | Corrosion | Evidence not stated | evidence stub: 'Inspection; programme'
KSIA-BFM-032 | Building & Facilities | Movement Joints | Evidence not stated | evidence stub: 'Inspection'
KSIA-BFM-033 | Building & Facilities | Façades & Glazing | Evidence not stated | evidence stub: "Inspection reports"
KSIA-BFM-034 | Building & Facilities | Terminal Finishes | Evidence not stated | evidence stub: "Site inspection"
KSIA-BFM-035 | Building & Facilities | Accessibility & Signage | Evidence not stated | evidence stub: 'Site inspection'
KSIA-BFM-038 | Building & Facilities | Building Maintenance | Evidence not stated | evidence stub: 'CMMS reports'
KSIA-EDM-002 | Energy & Demand Management | Energy Distribution | Evidence not stated | evidence stub: 'Licence / agreement'
KSIA-EDM-006 | Energy & Demand Management | Metering | Evidence not stated | evidence stub: 'Calibration certificates; register'
KSIA-EDM-007 | Energy & Demand Management | Tariffs & Billing | Evidence not stated | evidence stub: 'Bills vs meter data reconciliation'
KSIA-EDM-011 | Energy & Demand Management | Energy Consumption | Evidence not stated | evidence stub: 'Energy reports'
KSIA-EDM-013 | Energy & Demand Management | NMD | Evidence not stated | evidence stub: 'Demand profile data'
KSIA-EDM-017 | Energy & Demand Management | Solar PV Plant | Evidence not stated | NO evidence stated at all
KSIA-EDM-018 | Energy & Demand Management | Solar PV Plant | Evidence not stated | evidence stub: 'Monitoring data; CoC'
KSIA-EDM-020 | Energy & Demand Management | Energy Storage | Evidence not stated | evidence stub: 'Inspection'
KSIA-EDM-021 | Energy & Demand Management | BMS & Controls | Evidence not stated | evidence stub: 'BMS screenshots/logs'
KSIA-EDM-024 | Energy & Demand Management | Water | Evidence not stated | evidence stub: 'Water reports'
KSIA-EDM-026 | Energy & Demand Management | Emissions | Evidence not stated | evidence stub: 'Emissions report'
KSIA-PSR-001 | Process Safety & Risk | Hazard Identification & Risk Assessment | Evidence not stated | evidence stub: 'HIRA; risk register'
KSIA-PSR-002 | Process Safety & Risk | Hazard Identification & Risk Assessment | Evidence not stated | evidence stub: "MOC records"
KSIA-PSR-003 | Process Safety & Risk | Hazard Identification & Risk Assessment | Evidence not stated | evidence stub: "Risk register; verification evidence"
KSIA-PSR-004 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Evidence not stated | evidence stub: 'MHI RA; emergency plan; inspection'
KSIA-PSR-005 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Evidence not stated | evidence stub: "HAC drawings; Ex inspection records"
KSIA-PSR-006 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Evidence not stated | evidence stub: 'Inspection; drill records'
KSIA-PSR-007 | Process Safety & Risk | Standby Power Safety | Evidence not stated | evidence stub: 'Inspection'
KSIA-PSR-008 | Process Safety & Risk | Standby Power Safety | Evidence not stated | evidence stub: 'Inspection; certificates'
KSIA-PSR-009 | Process Safety & Risk | Emergency Preparedness | Evidence not stated | evidence stub: 'Plan; drill records'
KSIA-PSR-010 | Process Safety & Risk | Emergency Preparedness | Evidence not stated | evidence stub: "Inspection registers"
KSIA-PSR-011 | Process Safety & Risk | Emergency Preparedness | Evidence not stated | evidence stub: 'Investigation reports; trend'
KSIA-PSR-012 | Process Safety & Risk | Fire Safety Management | Evidence not stated | evidence stub: 'FRA; inspection'
KSIA-PSR-013 | Process Safety & Risk | Fire Safety Management | Evidence not stated | evidence stub: 'Fire-water assessment; site walk'
KSIA-PSR-014 | Process Safety & Risk | Fire Safety Management | Evidence not stated | evidence stub: "Permit records (sample)"
KSIA-PSR-015 | Process Safety & Risk | Hazardous Substances & Gas | Evidence not stated | evidence stub: 'Inventory; SDS; CoCs'
KSIA-PSR-016 | Process Safety & Risk | Hazardous Substances & Gas | Evidence not stated | evidence stub: 'Site inspection'
KSIA-PSR-029 | Process Safety & Risk | Statutory Appointments & Competencies | The question does the check's work | the row's own question asks whether this requirement is still live at all — it may be obsolete
KSIA-PSR-030 | Process Safety & Risk | Statutory Appointments & Competencies | Evidence not stated | NO evidence stated
KSIA-PSR-030 | Process Safety & Risk | Statutory Appointments & Competencies | The question does the check's work | the row's own question asks what this line is meant to test — ISO 14001, an internal policy, or something else. It cannot be audited as written.
KSIA-PSR-031 | Process Safety & Risk | Statutory Appointments & Competencies | The question does the check's work | the row's own question asks whether this is enterprise risk management or plant-level OHS risk assessment — two different auditees
KSIA-PSR-032 | Process Safety & Risk | Statutory Appointments & Competencies | The question does the check's work | the row's own question asks which of the two it is — the evidence required differs completely
KSIA-PSR-034 | Process Safety & Risk | Statutory Appointments & Competencies | Evidence not stated | evidence stub: 'Appointment letters; certificates'
KSIA-PSR-035 | Process Safety & Risk | Statutory Appointments & Competencies | Evidence not stated | evidence stub: 'Training matrix; rosters'
KSIA-PSR-036 | Process Safety & Risk | Contractor & Permit Management | Evidence not stated | evidence stub: 'Agreements; safety files; permits'
KSIA-PSR-037 | Process Safety & Risk | Incident Management | Evidence not stated | evidence stub: 'Incident register'

## Gaps by kind
Kind | Notes | Checks affected
Evidence not stated | 98 | 98
Duplicate or overlap | 56 | 56
No threshold to test against | 30 | 30
The question does the check's work | 10 | 10
More than one check in the row | 10 | 10
Conflict in the source | 8 | 8
Noted — nothing to inspect, correctly | 6 | 6
Wrong content on the row | 5 | 5
Other | 4 | 4

## Split or merge
ID | Discipline | Asset system | Requirement | Proposal
KSIA-ELE-009 | Electrical | AGL | AGL photometric/serviceability inspections, lamp outage within limits, secondary power switch-over verified; CCR maintenance. | photometric inspection, outage limits, switch-over and CCR maintenance are four tests
KSIA-ELE-011 | Electrical | Electricity Distribution System | Current single-line diagrams displayed in each switch room; protection grading/settings study available and applied. | a displayed diagram (Asset) and an applied protection grading study (Document) are different tests
KSIA-ELE-012 | Electrical | Electricity Distribution System | HV/MV cable routes marked, trenches/covers intact, cable test and thermography records; no unauthorised joints. | route condition (Asset) and thermography/test records (Document)
KSIA-ELE-017 | Electrical | Switchgear | Switching procedures, authorised persons (switching authority) register, arc-flash PPE and lock-out/tag-out available and used. | switching authority (Practice) and arc-flash PPE condition (Asset) in one row
KSIA-ELE-033 | Electrical | Generators | Day/bulk tank bunded, level alarms functional, spill kit available, fuel polishing/quality tests, no leaks. | bund condition and alarms (Asset) vs fuel quality tests (Document)
KSIA-ELE-043 | Electrical | FDS & Gaseous Suppression | Fire detection system serviced and certified; quarterly functional tests; gaseous suppression cylinder pressure/weight checks and room-integrity test. | detection servicing, suppression cylinder checks and room-integrity testing are three tests
KSIA-MEC-012 | Mechanical | HVAC | DB Earth leakage | one earth-leakage check scoped by asset system, not six near-identical rows
KSIA-MEC-016 | Mechanical | HVAC | Noise monitoring requirement by an AIA according to SABS 083 | one noise-survey check for the site; demarcation is separately MEC-104
KSIA-MEC-017 | Mechanical | HVAC | Chiller/AHU plant logs: set-points, ΔT, alarms cleared; controls in AUTO; refrigerant leak log; PER certificates for pressure equipment. | keep the plant-log half; the PER certificate is MEC-007 and the leak log is MEC-013
KSIA-MEC-018 | Mechanical | HVAC | Cooling towers/evaporative condensers: water treatment programme, cleaning & disinfection records, Legionella testing. | keep the water-treatment programme and cleaning records here; Legionella testing is MEC-008
KSIA-MEC-028 | Mechanical | People Movers | Lifts, escalators and travelators: annual inspection & comprehensive test by a registered Lift Inspector; register of lifts/escalators; certificates displayed. | keep only the register completeness and the displayed-certificate check — walk the terminal, count the units, reconcile against the register
KSIA-MEC-033 | Mechanical | Passenger Boarding Bridges (PLBs) | Structural assessment by an ECSA-registered Professional Engineer covering corrosion, welds, rotunda, tunnel and wheel bogie; remedial actions closed. | merge into MEC-032, and raise the missing PrEng requirement as a policy gap against ACSA rather than as a site non-compliance
KSIA-MEC-034 | Mechanical | Passenger Boarding Bridges (PLBs) | Auto-leveller, safety shoe, canopy, drive/steer and emergency stop tested; operator authorisation register; PM completed per OEM. | keep the demonstration here; the OEM test record is MEC-030; the operator authorisation register is a Document check of its own
KSIA-MEC-036 | Mechanical | Fuel System | A 3 yearly valid On-site Emergency Plan | split in two — the plan's currency and consultation with the local authority (Document), and the annual practical drill (Practice)
KSIA-MEC-046 | Mechanical | Fuel System | Pit lid integrity inspection (Anodising, seals and functionality) | one hydrant pit condition check covering box, chamber, lid, seals and couplers
KSIA-MEC-051 | Mechanical | Fuel System | Integrity inspection of electrical equipment in hazardous areas | keep the periodic inspection regime here; the Ex-certification of machinery is MEC-053
KSIA-MEC-052 | Mechanical | Fuel System | DB earth leakage, Wiring diagrams, COC | split three ways, or scope the single earth-leakage, diagram and CoC checks by asset system
KSIA-MEC-054 | Mechanical | Fuel System | Hydrant pit couplers, seals and pit lids intact; pits free of water/fuel; pit valve and lid inspection register maintained. | merge MEC-044, 046 and 054 into one hydrant pit condition check
KSIA-MEC-055 | Mechanical | Fuel System | Hydrant line pressure/tightness test records; emergency shut-down (ESD) push-buttons tested; bonding at fuelling positions. | delete the duplicated halves; keep bonding at fuelling positions as its own check
KSIA-MEC-056 | Mechanical | Fuel System | Tank in-service/out-of-service inspections, bund integrity & drainage, filter/water separator maintenance, product quality records. | split the bund and filter condition (Asset) from tank integrity (MEC-049) and product quality records (Document)
KSIA-MEC-062 | Mechanical | BHS | Sorter/Conveyor Interlock test records | merge into MEC-057, scoped to cover every interlock zone rather than a sample
KSIA-MEC-063 | Mechanical | BHS | Sorter siren test records | one siren check covering carousel and sorter
KSIA-MEC-065 | Mechanical | BHS | Guarding, emergency stops, lock-out procedure, conveyor PM completion rate, spares for critical drives. | split three ways — guarding and E-stops (already MEC-057/058/060), lock-out/tag-out procedure and its records (Practice), critical drive spares holding (Document)
KSIA-MEC-068 | Mechanical | Fire Protection - Fire Extinguishers | Annual service by SANS 1475-accredited provider; hydrostatic test dates; monthly inspection tags; correct type/location. | keep only 'correct type and location for the area's fire hazard class', which nothing else asks, and reconcile it against MEC-069
KSIA-MEC-077 | Mechanical | Fire Protection - Hose reels and fire hydrants | Annual flow/pressure tests; hydrant valve operation; hose reel condition; signage & access unobstructed. | keep signage and unobstructed access, which nothing else covers; the tests are MEC-071/072/074
KSIA-MEC-085 | Mechanical | Fire Protection - Fire Water pump station | Weekly churn test, annual flow test, diesel pump batteries/fuel, jockey pump & pressure logs; tank levels. | delete the duplicated halves; keep the churn test and the jockey pump as their own checks IF ACSA's manual actually requires them, which needs confirming first
KSIA-MEC-087 | Mechanical | Sewer, Potable & Stormwater Pumps | Earth leakage test | one earth-leakage check scoped by asset system
KSIA-MEC-089 | Mechanical | Sewer, Potable & Stormwater Pumps | Panel wiring diagram and COC validity check | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-091 | Mechanical | Gas Hot Water Facility | Sewer sump gas monitor calibration records | delete, or rewrite as an LPG gas-detection check and confirm against ACSA's hot water system task list first
KSIA-MEC-092 | Mechanical | Gas Hot Water Facility | Earth leakage test | one earth-leakage check scoped by asset system
KSIA-MEC-093 | Mechanical | Gas Hot Water Facility | Records of inspections for Guarding of moving parts | rewrite against the approved contractor task list for System - Hot Water (HWS) rather than inheriting the pump text
KSIA-MEC-094 | Mechanical | Gas Hot Water Facility | Panel wiring diagram and COC validity check | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-101 | Mechanical | Water Treatment Plant | Wiring diagram and COC validity check | one wiring-diagram-and-CoC check scoped by asset system
KSIA-MEC-102 | Mechanical | Water Treatment Plant | Earth leakage test | one earth-leakage check scoped by asset system
KSIA-MEC-105 | Mechanical | Water Treatment Plant | Noise monitoring requirement by an AIA according to SABS 083 | delete; one site noise survey check, with demarcation as MEC-104
KSIA-MEC-113 | Mechanical | Façade Access & Lifting Equipment | Cradles, hoists, MEWPs load-tested 12-monthly by registered LMI; lifting tackle register; operator competency. | keep only operator competency, which nothing else asks, and the displayed-tag check on cradles, hoists, MEWPs and lifting tackle
KSIA-CIV-003 | Civil | Markings | Check visiblity of markings | merge into CIV-001
KSIA-CIV-006 | Civil | Markings | Check visibility,dimensions, colour & background of Mandatory Information Markings | keep as one — mandatory markings warrant their own check, but say in the requirement that it is the mandatory subset of 002/003/004
KSIA-CIV-007 | Civil | Markings | Marking dimensions, colour, conspicuity and location comply; repainting programme; retro-reflectivity where applicable. | delete the condition half; keep only 'repainting programme exists and the interval per marking type is being met', which is a Document check
KSIA-CIV-008 | Civil | Visual Aids | Markings should be maintained in a conspicuous condition, readily visible to aircraft in the air or manoevering on the ground | delete
KSIA-CIV-011 | Civil | Visual Aids | Signs, PAPI siting/frangibility, wind indicators, obstacle marking/lighting per design; obstacle survey current. | split four ways: PAPI siting and frangibility (Asset); signs (already CIV-010); wind indicators (already CIV-012); obstacle survey currency within the 10 km radius (Document)
KSIA-CIV-019 | Civil | Runway | Asphalt Edge breaks | fold into CIV-018 as the edge check
KSIA-CIV-023 | Civil | Runway | Check Frangibility objects in Safety areas and Presence of Illegal Objects | split in two — frangible-mount certification of every registered object (Asset/reconcile), and a clear-strip sweep for unauthorised objects (Asset/examine)
KSIA-CIV-025 | Civil | Runway | Pavement condition (PCI) survey; cracking, spalling, joint sealant, rutting, FOD generation; repairs programmed. | keep as the document check — 'PCI survey current within 3 years and every distress it records carries a programmed repair' — and let 016/017/019 carry the condition
KSIA-CIV-026 | Civil | Friction Measurement & Corrective Maintenance | measurements of friction charecteristics of a runway surface and corrective maintenance when the friction charecteristics are below minimum friction levels | merge with CIV-024
KSIA-CIV-030 | Civil | Taxiways & Taxilanes | The surface is maintained in such a condition such as to prevent formation of harmful irregularities | consider one pavement-condition check scoped to a surface, rather than three identical checks
KSIA-CIV-035 | Civil | Taxiways & Taxilanes | Asphalt Edge breaks | fold into CIV-034
KSIA-CIV-038 | Civil | Taxiways & Taxilanes | Taxiway/taxilane pavement condition, edge drop-offs, shoulders, joint sealing; centreline markings. | delete
KSIA-CIV-045 | Civil | Aprons | Apron surface condition, joint sealant, fuel/oil contamination, spillage clean-up procedure, tie-down/grounding points. | split the spill-response half out as a Practice check — 2-hour containment, disposal records retained 5 years — and leave condition and grounding points as the Asset check
KSIA-CIV-047 | Civil | Pavement Strength | PCN published and supported by current pavement evaluation; overload approvals controlled. | merge into CIV-014, keeping only the overload-approval control as its own line
KSIA-CIV-051 | Civil | Drainage | Stormwater drains, culverts and channels clear; inspection register; oil/water separators serviced; no ponding on movement areas. | keep only the oil/water separator half and make it a Document check — annual efficiency test, sludge depth under 25% of chamber depth, disposal records retained 5 years
KSIA-CIV-054 | Civil | Inspections | Daily movement-area serviceability inspections logged; defects reported and closed; wildlife/FOD reports. | keep only the defect-closure loop; the frequency is CIV-052
KSIA-CIV-056 | Civil | Perimeter / Security Fence | Security fence integrity, clear zones, patrol/inspection records, gates and access control functional. | split the patrol and inspection record half out as a Document check — weekly gate checks, monthly condition monitoring, fence voltage tests against the design range
KSIA-BFM-006 | Building & Facilities | Certificates | Occupancy certificates, local-authority fire compliance, electrical CoC per building and lift/escalator certificates available and current. | four certificate families with four different issuers and intervals in one row
KSIA-BFM-030 | Building & Facilities | Refuse Disposal | Waste areas hygienic, licensed removal contractors, recycling/general waste records, pest control. | hygiene (Asset), contractor licensing (Document) and pest control in one row
KSIA-EDM-013 | Energy & Demand Management | NMD | Maximum demand never exceeds Notified Maximum Demand; NMD penalties tracked; load-shedding/peak strategy. | NMD compliance (a figure) and demand-management practice are two different tests in one row
KSIA-EDM-018 | Energy & Demand Management | Solar PV Plant | PV performance ratio monitored; inverter and panel maintenance/cleaning records; PV installation CoC; earthing/lightning protection. | PR monitoring, maintenance records, CoC and earthing/lightning protection are four tests in one row
KSIA-EDM-019 | Energy & Demand Management | Energy Storage | • Grid Connection - agreement with utility to export • Land rights - submission to the council • Environmental - depending on technology. Hydro one must comply with regulations under water section and battery storage must comply with • Wheeling agreements | four approval types, four different authorities
KSIA-PSR-004 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Fuel farm: MHI notification & risk assessment, emergency plan, bund/containment, hydrant pit lids preventing water ingress and environmental contamination. | MHI notification and risk assessment (Document) sit in the same row as bund and pit-lid condition (Asset) — two different failures, one row
KSIA-PSR-006 | Process Safety & Risk | Fuel Farm & Hydrant (MHI) | Spill response equipment at fuelling positions and fuel farm; oil/water separators serviced; spill drills conducted; environmental incident records. | spill equipment condition, separator servicing and drill records are three tests
KSIA-PSR-008 | Process Safety & Risk | Standby Power Safety | Bulk diesel storage compliant: bunding, tank certification, fire separation from generator, spill containment, dispensing controls. | tank certification is a Document test inside an Asset row
KSIA-PSR-012 | Process Safety & Risk | Fire Safety Management | Fire risk assessment current; fire compartmentation/doors, escape routes clear, fire equipment access; fire marshal appointments. | fire risk assessment and marshal appointments (Document) vs compartmentation and escape routes (Asset)
KSIA-PSR-015 | Process Safety & Risk | Hazardous Substances & Gas | Hazardous chemical inventory, SDS available, storage segregation & ventilation, LPG installations certified, confined-space & hot-work procedures. | inventory and LPG CoCs (Document) vs storage segregation and ventilation (Asset)
KSIA-PSR-024 | Process Safety & Risk | Statutory Appointments & Competencies | Aerodrome lighting and power back up systems maintenance - ICAO | AGL outage limits (Asset) and standby changeover records (Document) in one row
KSIA-PSR-034 | Process Safety & Risk | Statutory Appointments & Competencies | GMR 2(1), 16(2), electrical (EIR/EMR) and LI/LMI appointments in writing, current, with competency evidence. | GMR 2(1), 16(2), EIR/EMR and LI/LMI are four separate statutory appointments in one row